## HT FEEDER
Format for Technical Pre-Bid Queries
Tender No: TPNODL / OT/ 2021-22/066
Package Name : 33/11KV Feeder
Sr. No. | Detailed Reference to Tata Power Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | Tata Power Response
1 | 2 | 3 | 4 | 5
1 | Clause no. 4.1 | Clause No. 4.1 Three Phase Four Wire, AC Static Current Transformer (CT) and Voltage Transformer (VT) operated Watthour and Var-hour Energy Meter. It consists of measuring elements(s), time of use of register(s) and display and plug in type bi-directional communication module all integral within the meter housing. The meter design shall be such that only CT MF is required energy calculation. | We understand that the requirement of plug in type bi-directional communication module all integral within the meter housing is not in the scope of this tender. Request you to please amend the same. | ok
2 | Clause no. 4.03 Annexure-I | Clause No. 4.03 a. For 11kV – Ib = 1A; Imax= 10 Amps (Balanced and Unbalanced Load) b. For 33/66kV/220kV – Ib shall be 1A (shall be defined in tender) When Ib= 1A; Imax= 2 Amps (Balanced and Unbalanced Load) | Please confirm the requirement- Offered meter have two variant 1) Ib = 1A; Imax= 2 Amps 2) Ib = 5A; Imax= 10 Amps Please confirm the same for requirement of 11 KV rating Please accept the same. | ok
3 | Clause no. 4 Annexure-I Unbreakable, high grade, fire retardant reinforced Insulating material (protective Class II) with FV0 Fire Retardant, self - extinguishing, UV stabilize, recyclable and Anti oxidation properties | Clause No. 4.15 Resistance to heat and fire The terminal block and Meter case shall ensure safety against the spread of fire. They shall not be ignited by thermal overload of live parts in contact with them as per clause 6.8 of IS 14697 fire retardant material shall be used. | Terminal block is most important part as it undergoes thermal stresses due to over current/heating. Our meter’s terminal block is V0 compliant plastic. Meter enclosure and terminal cover are made of LEXAN 143 or equivalent material FV2 Compliant. It has to be noted that over current related heating affects the terminal block most. Not the meter cover or terminal cover. Same should be acceptable | ok
4 | Clause no. 4 | Clause No. 4.23 Self-Diagnostic feature The meter shall have logging with date and time in memory for un satisfactory / non-functioning of 1. Real Time Clock 2. RTC battery 3. Non Volatile Memory | Status of RTC & NVM will be available on meter display under “self diagnostic “display parameter. Also in case of NVM & RTC failure meter will log the same as event along with date & time. Status of RTC & NVM not available at BCS ends in healthy condition. Self diagnostic will be available on Display only, as describe below:- Self diagnostic check 00: Healthy, 01: NVM Fail, 02: Battery Fail, 03: Both Fail Same should be acceptable. | ok
5 | Clause No 4.26 Annexure-I serial no. 2 Depth of terminal hole :20 | Clause No 4.26 Internal diameter of the terminal holes 5 mm ( minimum ) Depth of the terminal holes 20 mm (minimum) Annexure-I serial no. 2 Depth of terminal hole :20 | Depth of the terminal holes is approx.. 18 mm. Please accept the same. | ok
6 | Clause no. 4 | Clause no. 4 4.29 Display a. Backlit LCD, Scrolling, 10 seconds for each Parameter minimum 8 digits LCD display. | In offered meter, 7 segment 7 digit displays will be provided. Same should be acceptable. | ok
7 | Clause no. 4 | Clause No 4.30 Software and communication compatibility The bidder shall supply software required for communication through MRI and BCS software including required training to use the software free of cost. The meter shall be compatible to communicate with GSM/GPRS/RF modems in DLMS protocol. | Offered meter comply as per IS: 15959. The meter will have facility to data transfer locally through CMRI and remotely through GSM/GPRS Modem only as per DLMS protocol. We understand that supply of external modem is not in the scope of this tender. Please confirm the same. | ok
8 | Clause no. 4 | Clause No 4.32 Usage Application Outdoor | Indoor only. For outdoor application Meter box required If same is required please provide the specification of box and amend BOQ accordingly. | ok
9 | Clause no. 4 | Clause No 4.34 Harmonics recording The meter should record the current and voltage THD. The meter should record harmonics up to 20th harmonic Average THD of all phase for voltage THD and current THD. THD values shall have 30/15 minutes (as applicable) integration period in load survey. Accuracy of harmonics recording shall be as per meter accuracy class. The meter shall generate a flag whenever the threshold (user configurable) of the 5% THD of the load current and voltage is breached. | In offered meter, THD voltage event & THD current event is available, limit will be factory configurable only. Same will not available in load survey. Limits for measurement & logging of THD Voltage & current is available in event logging. However meter also have display parameter to show phase wise voltage , current & power THD. THD is not supported in load survey. | As per our sepecification
10 | Clause no. 4 | Clause No. 4 4.31 Software & communication capability: The meter shall be compatible to communicate with GSM/GPRS/RF modems in DLMS protocol. Clause No. 4.1 Communication capabilities and software feasibilities: 4.1.1 The meter shall have facilities for data transfer locally through MRI (Using optical port/RJ11/RF modems) and remotely using optical port/RJ11 port via GSM/GPRS/RF modems with proper security through optically isolated ports through serial communication. 4.1.2 Meter should have additional RJ11/ RJ45 port to communicate with GSM/GPRS/RF modems. 4.1.5 Bidder should also provide protocol / API for hosting in smart modem using GPRS / RF technology for capturing full data / partial data from the meter and sending it to server / HES OTA. | Offered meter comply as per IS: 15959. The meter will have facility to data transfer locally through CMRI and remotely through GSM/GPRS Modem. We understand that supply of external modem is not in the scope of this tender. Please confirm the same. | As per our sepecification
11 | Clause no. 4.1 | Clause No. 4.1 Communication capabilities and software feasibilities: 4.1.6. Bidder should provide software for changing firmware of meters in mass. Any software/keys required to reprogram the meter and any other support for enabling TPNODL to execute option will be provided without any additional cost to TPNODL. 4.1.9 Bidder to supply protocol to read the meters supplied against this tender using intelligent RF/GPRS/GSM modem with store and forward feature without any additional cost implication. Bidder to provide API on MIOS standard to convert the meter data in to XML and read API for hosting in server and modem RF/GSM/GPRS based for reading meters from any third party manufactured modems. Bidder to provide necessary support if required during integration of the RF modem with supplied meters against this tender. | Offered meter comply as per IS: 15959. We do not recommend firmware change of the meter however meter configuration changes allowed by IS 15969 are possible, e.g. TOD, Billing date etc. We will provide windows based common meter reading API for meter reading which will run at head end system and perform in transparent mode. We will provide MIOS based XML file of meter data, However integration is not in our scope. Please confirm the same. | As per our sepecification
12 | Clause no. 4.2 | Clause: 4.2.1 Magnetic field : Meter shall be immune to magnetic field such that it shall not affect the normal overall functionality however, in case of abnormal magnetic field as defined below meter shall perform as per the following actions: a) Meter shall log the event in its memory as “MAGNET” with snapshot and the event logging threshold values as per table no. 1 in 4.4 b) The energy recording to shift on Imax, Vref with UPF. | Meter with compliance to CBIP 325 for influence of magnetic induction shall also be acceptable. Meter would be immune and within permissible accuracy limits as per CBIP 325 and if meter gets affected it will log magnetic event with date and time and start recording at I Max. Magnet P time for occurrence & restoration shall be 20-30 secs approx. to avoid tampering through any timer based tampering methods. Specific Legend will be available on LCD of meter as below:- Suitable abbreviation/information will also provided under “present status other then CT & PT related events”. Display parameter. Same should be acceptable. | As per our sepecification
13 | Clause no. 4.2 | Clause: 4.2.1 Magnetic field : Abnormal magnetic field is defined as below: a) Continuous DC magnetic induction: >0.20 Tesla±5% (value of the magneto motive force to be applied shall be generally>10000 AT) | Meter will compliance to CBIP 325 for influence of magnetic induction will also be acceptable. Immunity level up to 0.5 T & 0.2Tis not guaranteed; Either Meter would be immune and if meter gets affected it will log magnetic event with date and time and start recording at I Max. Specific Legend will be available on LCD of meter | As per our sepecification
|  | Clause: 4.2.1 Magnetic field : Abnormal magnetic field is defined as below: b) AC magnetic induction: >10 mili Tesla (if produced with circular metal core with square cross section as specified in CBIP latest report with 2800 AT) |  | As per our sepecification
|  | Clause: 4.2.1 Magnetic field : Abnormal magnetic field is defined as below: c) Permanent magnet: Immune up to 0.5T and event logging> 0.5T |  | As per our sepecification
14 | Clause no. 4.2 | Clause: 4.2.2 Electrostatic Discharge (ESD) Meter shall be immune up to 50KV and shall record accurate energy as per IS: 13779:1999/CBIP 325. Meter shall log the event into memory as ESD with date and time stamp for any ESD greater than 50KV with snapshot, the event logging threshold values as per table 1 in 4.4. | Offered meter will be immune under influence of spark up to 35KV. However the meter immune up to certain high level of spark. “Abnormal external interference” event with date and time stamp will indicate ESD tampering. Offered meter is as per previous supplies, it is kindly requested to accept the same. | As per our sepecification
15 | Clause no. 4.2 | Clause: 4.2.4 Meter should be immune to high/low frequency devices. Meter shall log the event in its memory as “Jammer” with date and time stamp with snapshot, the threshold values as per table no. 1 in 4.4. | Against any external interference devices offered meter will complies as per IS 13779 & CBIP 325. “ Meter will be immune to high/low frequency. If it gets affected, it will log event “abnormal external interference. | As per our sepecification
16 | Clause no. 4.2 | lause No. 4.2.5 The meter should be immune or log the tamper on application of any other higher magnetic field of any frequency waves, micro waves like magnetron etc. | This is very specified & non standard requirement under such influence meter may behave abnormally, it may be immune or permanently damage Offered meter will complies as per IS 13779 & CBIP 325. If it gets affected, it will log event “abnormal external interference. | As per our sepecification
17 | Clause no. 4.3 | Clause 4.3.2 4.3.2 The meter shall not saturate on passage of direct current, which can cause the meter either to stop recording/ record inaccurately. DC injection shall be tested both in phase and neutral. Measurement by meter shall not get influenced by injection of Chopped signal/ DC signal/ DC pulse upto 330V and for any value beyond this. Meter shall log the event into memory as ‘Neutral Disturbance’ with date & time stamp the thresholds are as per table no. 1 in 4.4 | Meter will remains either immune or if it gets affected metering functionality log ND event & record energy at V-ref X Actual current X UPF. Accuracy will be ±4%. Specific Legend can be provided on LCD of meter Offered meter is as per previous supplies, it is kindly requested to accept the same. | As per our sepecification
18 | Clause no. 4.4 | Clause No. 4.4.1 The meter shall record forward energy under all abnormal tampering conditions and shall be capable of recording occurrence and restoration of abnormal events listed below along with the date and time and snapshot of individual voltages, current, power factors, active energy and apparent energy at the time of occurrence of abnormal event and restoration of normal supply. | Events will log as per prevailing electrical conditions. Offered meter have event logging as per IS: 15959. However if case meter record tamper, it will log snap shot on confirmation of event i.e. either occurrence or restoration. Considering restoration & occurrence events as separate event. Snap shot will be Voltage, Line current, Neutral current & configured energy. It is kindly requested to accept the same | As per our sepecification
19 | Clause no. 4.4 | Clause No. 4.4.2 The time stamp and snapshot parameters shall be recorded at the start time of event of occurrence (T1) and for restoration the time stamp and snapshot parameters shall be recorded at the end time of the event (T3). | Offered meter have event logging as per IS: 15959. However if case meter record tamper, it will log snap shot on confirmation of event i.e. either occurrence or restoration (after Persistence –time). Snap shot will be Voltage, Line current, Neutral current & configured energy. | As per our sepecification
20 | Clause no. 4.4 | 4.4.4 Multiple occurrences of same event, with different time stamps should not be logged without restoration of first occurrence, except for the case of Top Cover Open. | Offered meter have event logging as per IS: 15959. The tamper events will be stored in relevant compartment (i.e. All voltage related event will be logged in one compartment) on FIFO basis limited to no. of event assigned to that compartment. Occurrence & restoration event consider as separate event. So availability of unrestored/restored events details will depends upon nos. of tamper events assigned to relevant compartment. | As per our sepecification
21 | Clause no. 4.4 | Clause no. 4.4.7 The meter shall record in export registers in case of reversal of all CT terminals. The meters are to be used for registration of energy consumed by the consumer, as such the meters shall be programmed for import mode and in case of reversal of energy direction (reversal of all CT terminals) meter shall register energy separately in export mode i.e. in case of CT reversal, meter shall record scalar (not vector sum) sum of energy. | The meter will record in forward direction in case of reversal of all CT terminals. In case of one, two or all three CT reversal offered meter will register energy in Active export under CT reverse register along with the forwarded energy register. | As per our sepecification
22 | Clause no. 4.4 | Clause no. 4.4.8 The meter shall register correctly if supply neutral is not available at the meter neutral terminal. The meter shall work in absence of any two incoming wires. It shall keep recording correctly in case of unbalance system voltage also as defined above. | Meter will record energy & event as per prevailing electrical conditions | ok
23 | Clause no. 4.5 | Clause 4.5 Event Compartments | The tamper events will be logged in their respective compartment as per IS15959:- 1) Voltage related event -150 Nos. 2) Current related events – 150 Nos. 3) Other Events -150 Nos. 4) Non roll over – Cover open (5 nos.) 5) Power failure – 50 Nos. Occurrence event and restoration event taken as separate event. Same should be acceptable. | ok
24 | Clause no. 4.5 Annexure-I serial no. 4 | Clause 5.0 General constructions Battery: Guaranteed life of 15 years Annexure-I serial no. 4 Battery: Guaranteed life of 15 years | Operating life of battery would be 10 years. | ok
25 | Clause no. 5.10 Annexure-I serial no. 1 | Clause 5.1 Meter Body 5.1.1 The meter body shall be made of unbreakable, high grade, fire retardant, reinforced insulating material (protective class II) with FV0 Fire retardant, self extinguishing, UV stabilize, recyclable and anti oxidation properties. 5.1.3 Meter base shall be opaque with polycarbonate LEXAN 500R or equivalent on prior approval from TPNODL. 5.1.4 Meter cover shall be transparent with polycarbonate LEXAN 143R/943A or equivalent on prior approval from TPNODL. Annexure-I serial no. 1 a) Base: Opaque with polycarbonate LEXAN 500R or equivalent b) Cover: Transparent with polycarbonate LEXAN 143R/943A or equivalent | The meter case cover & base and ETBC will be FV2 Compliant & Meter terminal will be FV0 compliant. Offered meter have opaque meter base & terminal block and transparent meter cover. However material will be: Meter case base & cover: LEXAN 143 or Equivalent Terminal Block: LEXAN 500R/equivalent | ok
26 | Clause no. 5.1 Annexure-I serial no. 1 | Clause 5.1 Meter Body 5.1.2 The minimum thickness of the meter enclosure shall be 2mm. Annexure-I serial no. 1 Thickness, Min. 2.0 mm | Thickness will be approx 2mm ± 0.2mm. | ok
27 | Clause no. 5.2 Annexure-I serial no. 2 | Clause no 5.2.3 Terminal block and terminal cover shall be of a material which complies with the requirements of IS11731 (part 1) method FH1. The material of which the terminal block is made shall be capable of passing the Heat Deflection temperature test given in ISO 75 for temperature of 135°C and pressure of 1.8 MPa as mentioned in IS 14697. Tested as per ISO 75-2/A or ASTM D648. Terminal block and terminal cover shall be of a material which complies with the requirements of IS11731 (part 1) method FH1. The material of which the terminal block is made shall be capable of passing the Heat Deflection temperature test given in ISO 75 for temperature of 135°C and pressure of 1.8 MPa as mentioned in IS 14697. Tested as per ISO 75-2/A or ASTM D648 | Only Terminal block is most important part as it undergoes thermal stresses due to overcurrent/heating. Complies with HDT limit of 135 deg C should only applicable for terminal block . Same should n't be mandatory for terminal cover . | ok
28 | Clause no. 5.2 | Clause no. 5.2.7 Temperature sensor to be for sensing the temperature and meter should be programmed in such way that on reaching the threshold value set (as per tamper table no. 1) the event must get logged. | As per IS 15959 Temperature rise event is not defined, hence same is not provided. | ok
29 | Clause no. 5.2 | Clause No. 5.2.7 To get the desired temp rise & avoid hot spots the design of the each terminal screw, terminal screw shall be an Allen screw head & shall be operated with allen key only. Size of the allen screw is 8mm dia. | Terminal block have barrel type design, terminal screw will be cheese head type & can be operated with screw driver. Screw will provided same as previous supply. It is kindly requested to accept the same. | ok
30 | Clause no. 5.2 | Clause No. 5.2.9 Terminals shall be preferably with Allen screw with at least 8 mm dia for better contact area. Terminal & screw should not be damaged during regular opening and tightening. (MS terminals not accepted)) Clause 5.2.13 terminals shall be provided with Zinc plating or tinning or suitable compatible coating to avoid the bimetallic effect at the joints with AL core of cable. | For better grip of conductors barrel type design will be provided and terminals will be made up of Brass for better conductivity. Connecting terminal: Brass Terminal Screws: nickel plated brass | ok
31 | Clause No. 5.1/ | Clause No. 5.3 Terminal cover 5.3.1 Terminal cover will be short type & transparent with virgin polycarbonate LEXAN 143A/943 or equivalent material. 5.3.2 The terminal cover should be of short type 20 to 25mm length 5.3.5 The terminal cover design should be such that sealing screw locking provision on cover should have min dimension of 3mmx3mm (excluding seal lock hole) | Terminal cover will be transparent with polycarbonate LEXAN 143A/943 or equivalent material. Terminal cover will be extended type & ETBC to Terminal bottom will be approx 40-45mm. In offered meter, Suitable arrangement will be provided. Sealing holes on sealing screw is sufficient to accommodate lash wire of seal However hole dia will be approx 2mm | ok
32 | Clause No. 5.6 | Clause no. 5.6 MD Integration: The MD integration period shall be 30/15 minutes (integration period-programmable by CMRI at site and also thru AMR with adequate security level). The MD resetting shall be automatic at the 1st of the month i.e. 0000 hours of 1st day of the month. Manual MD reset button shall not be available. Last 12 MD values shall be stored in the memory. MD shall be recorded and displayed with minimum three digits before decimal and minimum two digits after decimal points. MD integration shall be of sliding Type at an interval of 10 min. | Sliding window internal will be 1/3 rd of DIP. I am requesting you please amend accordingly, we are providing better option. | ok
33 | Clause No. 5.7 | Clause no. 5.7 Parameters in BCS All these parameters (mention below clauses) shall be downloaded locally or remotely and interpreted in PC/Laptop. | For remote external modem will required, however, we understand modem is not in our scope. | ok
34 | Clause No. 5.7.1 | Clause 5.7 Load survey: The meter shall be capable for recording 30 min. average of the following parameters for 60 days: 1)Termperature near terminal blok 2)THD volatge phase wise 3)THD current phase wise | This is very specified requiremen, same shouldn't be mandatory requirement. Limits for measurement & logging of THD Voltage & current is available in event logging. However meter also have display parameter to show phase wise voltage , current & power THD. Same should be acceptable | ok
35 | Clause No. 5.7.1 | Clause 5.7 Load survey: The meter shall be capable for recording 30 min. average of the following parameters for 60 days: 1. Voltage per phase 2. Current per phase 3. Power Factor per phase 4. Average kWh 5. Average KVAH 6. kVArh (lag) 7. kVArh (lead) | Calculated power factor will be available in load survey instead of phase wise power factor. | ok
36 | Clause No. 5.7.2 | Clause No. 5.7.1 Load survey: Meter shall be capable of recording daily Energy and Demand 00:00 to 24:00 Hrs kWh/kVAh, kW/kVA in BCS for 60 days. Midnight energy value of cumulative kWh/kVAh and daily consumption kWh/kVAh should be available in meter memory for last 90 days. | Offered meter records cumulative kWh for mid night energy & load survey for 60 days as per IS 15959. User can manually calculate the consumption for configured energy. | ok
37 | Clause No. 5.7.2 | Clause No. 5.7.2 Load survey: Meter shall be capable for following instantaneous parameters in memory and should be available in BCS. Meter date & time DD MM YYYY HH MM SS MRI/PC date & time DD MM YYYY HH MM SS Dump date & time DD MM YYYY HH MM SS | Following parameters will be available:- Meter date & time (dd / mm/ yyyy HH MM SS) & Meter reading date & time (dd /mm/ yyyy HH MM SS) will be available | ok
38 | Clause No. 5.7.2 | Clause No. 5.7.2 Meter shall be capable for following instantaneous parameters in memory and should be available in BCS. Cumulative Power OFF duration 00000 Cumulative Power On duration. 00000 | Cumulative Power OFF duration & Cumulative Power On duration will be available in form of (YY DDD HH MM). | ok
39 | Clause No. 5.7.2 | Clause No. 5.7.2 Meter shall be capable for following instantaneous parameters in memory and should be available in BCS. Terminal block temperature | This is very specified requiremen, same shouldn't be mandatory requirement. Not available in instantaneous parameters. | ok
40 | Clause No. 5.7.2 | Clause No. 5.7.2 Meter shall be capable for following instantaneous parameters in memory and should be available in BCS. Last Billing date dd:mm:yyyy | Not available in instantaneous parameters Billing date will be available in Reading parameter & Average temperature of meter will be available in LS at BCS end | ok
41 | Clause No. 5.7.3 | Clause No.5.7.3 General information Manufacture date (MM/YYYY) TOD Profile profile showin timming and seasons | Manufacturing Year will be available & TOD profile showing timing and seasons are not available. Only TOD profile will be available in TOD data at BCS end | ok
42 | Clause No. 5.7.4 | Clause no. 5.7.4 Billing Parameters TOD details with day time and season wise. | TOD profile showing timing and seasons are not available. Only TOD profile will be available in TOD data at BCS end | ok
43 | Clause No. 5.7.6 | Clause no. 5.7.6 Tamper events The meter should not have any other events logging or any logic other than desired in specs | This is specified requirement, Each & every manufacturer have different specified logics for tamper. Please amend accordingly | ok
44 | Clause No. 5.8 | Clause 5.8 Display units The LCD display shall have a wide viewing angle of 120 degree. The Wh & VAh register shall have minimum 8 digits LCD display and size of the digits shall be minimum 10mmx5mm.Cumulative energy (Wh & VAh) shall be displayed without decimal in auto scroll mode. (However decimal shall be available in push button mode for high resolution display for testing). | It is requested to accept viewing angle of minimum 60 degree. .7 digit display with digit size of 10mm x 5 mm Resolution for energy, demand will depends upon commissioning of meter. | ok
45 | Clause No. 5.8.1 | Clause No. 5.8.1 Push mode: Cum. Wh Cum. VAh High Resolution Wh High Resolution Vah High Resolution VARh (Lag) High Resolution VARh (Lead) | Energy will be in KWH/MWH depending on comissioning of CT & PT.Same can be finialized after mutual consent between buyer & purchaser | Energy should be in wh. We are using 1A CT.
46 | Clause No. 5.8.1 | Clause No. 5.8.1 Push mode: ESD tamper count Latest ESD tamper occurrence date Latest ESD tamper occurrence time TC Open occurrence date of very first event TC Open occurrence time of very first event Latest Magnetic tamper occurrence date Latest Magnetic tamper occurrence Time | Offered meter will be immune up to 35KV spark and HV as per relevant standard. Tamper details will be available in following display parameters: • Present status of CT events • Present status of PT related events • Present status other then CT & PT related events • First occurred tamper • Date of first occurred tamper • Time of first occurred tamper • Last occurred tamper • Date of last occurred tamper • Time of last occurred tamper • Last restored tamper • Date of Last restored tamper • Date of Last restored tamper •TC Open occurrence date of last event •TC Open occurrence time of last event Suitable information /abbreviation will be provided at display under” Present status other then PT & CT”. Same should be acceptable | ok
47 | Clause No. 5.9.1 | Meter constant shall be indelibly printed on the name plate as imp / Wh & imp/VArh. Meter constant shall be as per actual without multiplying factor. | Meter constant is depended on Commissioning of meter. It may be in KV/MW/WH. Same can be finialized after mutual consent between buyer & purchaser | Metre should be Wh type.
48 | Clause No. 6 | Clause 6.0 Name plate and marking The base color of name plate shall be blue (as of TPC) | Rating plate information’s will be laser printed on rating plate as per IS: 1497. Base of rating plate will be off white & character will black in color It will be same as previous supply of Tata power. | ok
49 | Clause No. 6 | However the following shall be printed in bar code on the meter nameplate (shall be laser printed on name plate instead of any sticker). All data shall be laser printed on meter along with Sr.NO and date of manufacturing. No sticker to be used to avoid loss of data in event of fire. Content Format for bar code: TPNODL MMYY XXXXXXXX (8-digit Serial no.). The PCB Serial number should be printed on the PCB instead of sticker. | The meter will have manufacturer specific 8 alpha-numeric digit serial no. & Barcode will contain manufacturer specified meter Sr. Nos. only (laser printed). All other information will be laser printed on rating plate. Same should be acceptable. | ok
50 | Clause No. 7.3 | Clause 7.3 Acceptance test | Acceptance test will be performed as per IS 14697 | ok
51 | Clause No. 7.5 | Clause 7.5 Special Test: The bidder shall ensure that API is compatible with TPC’s CFW. | Offered meter comply as per IS: 15959. Open protocol Same as per previous supply | ok
52 | Clause No. 9 | Clause No. 9.0 i)1 no. leaflet with each meter | Same will be provided in softcopy. | One leaflet with each meter
53 | Clause No. 11 | Clause No. 11 Guarantee Bidder shall be further be responsible for free replacement at site for another period of Three years from the end of the guarantee period for any latent defects if noticed and reported by the TPC. | Offered meters will be guaranteed for a period for 5 years from the date of supply. No additional
54 | Clause No. 12 | Clause no. 12 PACKING 2. Individual meter should be packed in separate box. Routine test report (with manufacturing company logo) of the individual meter shall be kept inside each card board carton of the meter. | Packing will be as per previous supply for Tata power. | ok
55 | Clause No. 12 | Clause no. 12 PACKING On back side of routine test certificate (RTC) the bidder shall print a picture of the meter with its small details like for consumer to know about meter. | Serial no. of meter will be provided in Routine test certificate, Picture of meter will not provided. | ok
56 | Clause No. 13 | Tendering stage: Bidders are required to manufacture 03 numbers of sample meters as per the TPNODL specification (sealed, unsealed and open able base and cover to view/test the inner circuits) and submit the samples (non-returnable) along with bid for approval. These samples should be submitted at TPNODL store. | We are requesting please waive off the sample requirement, as we are regular supplier of Tata power | As per our sepecification
57 | Clause No. 14 | Clause No. 14 Quality Control Prior to final testing and calibration, sample meters shall be subjected to aging test (i.e. meters will be kept in ovens for 24 hours at 55 Deg. C temperature and atmospheric humidity under real-life condition at its full load current. After 24 hours meter should work satisfactorily. | This test is not performs at our works. | As per our sepecification
58 | Clause No. 18 | Clause no. 18. Spares, accessories & tools 1. Bidder to be provides free of cost 02 nos of jig for retrieving data from memory of the meter with every new design of the meter in which previous jig is supplied cannot be used. Jig should be such that NVM can be push fit on this jig & data can be retrieving from this NVM. | No JIG will be provided. If required data can be retrieved at our works. | As per our sepecification
59 | Clause No. 18 | Clause no. 17 Spares, accessories & tools Five (5) nos. of optical cord against each 100 meter lot for retrieving the data of meter through optical port should be provided, if design of optical port is changed from those of previously supplied meters. | Please provide about communication required:- • Optical to DB( male) • Optical to USB Please confirm & amend accordingly | Optical to USB
60 | Annexure-I Inspection test plan | Serial no. 17 All tests as defined in IS 15959 (Part- 2):2011 | It seems there is tophography error, IS15959 part:-1 is applicable for Smart WC meter. Please clarify & ammed accordingly. It should be IS15959 part-1 | ok
61 | Annexure-I Inspection test plan | Serial no.18Communication between Meter and MRI; MRI & BCS Software:-IS16444 Part2 | It seems there is tophography error, IS16444 part:-2 is applicable for Smart meter. Please clarify & ammed accordingly. It should be IS14697 | ok
62 | 3 | CLIMATE CONDITIONS OF THE INSTALLATION d) Maximum Humidity : 100% e) Minimum Humidity : 10% | d)Maximum Humidity : 95% | ok
63 | 4.03 | Basic Current (Ib) & rated Maximum current (Imax) a. For 11kV – Ib = 1A; Imax= 10 Amps (Balanced and Unbalanced Load) b. For 33/66kV/220kV – Ib shall be 1A (shall be defined in tender) When Ib= 1A; Imax= 2 Amps (Balanced and Unbalanced Load) | 1-10A can't be provided. 5-10A or 1-2A is only supported. | ok
64 | 4.26 | Internal diameter of the terminal holes Depth of the terminal holes 5 mm ( minimum ) 20 mm (minimum) | Diameter : 5.5mm +/-0.2 mm Depth: 15 mm +/- 0.5 mm | ok
65 | 4.34 | Harmonics recording The meter should record the current and voltage THD. The meter should record harmonics up to 20th harmonic Average THD of all phase for voltage THD and current THD. THD values shall have 30/15 minutes (as applicable) integration period in load survey. Accuracy of harmonics recording shall be as per meter accuracy class. The meter shall generate a flag whenever the threshold (user configurable) of the 5% THD of the load current and voltage is breached. | Accuracy of harmonics recording can't be guranteed as per meter accuracy class. Only accuracy of energy can be measured and it ill be as per accuracy class. | ok
66 | 4.35 | Terminal arrangement The terminal pin shall be 10 terminal arrangement with phase voltage terminal in between current terminals as mentioned in clause no. 5.2.11 | Standard SEIPL terminal arrangement will be provided. Voltage in the top row and current in bottom row. | ok
67 | 4.1.1 | The meter shall have facilities for data transfer locally through MRI (Using optical port/RJ11/RF modems) and remotely using optical port/RJ11 port via GSM/GPRS/RF modems with proper security through optically isolated ports through serial communication. | Modems can be plugged externally to RS232 Port | ok
68 | 4.1.5 | The bidder shall supply software required for local (MRI/Laptop) & remote (AMI) connectivity including required training to use the software free of cost. Bidder shall provide the communication protocol / APIs as per MIOS standards for communication with meter through local (MRI) / BCS as and when required by TPNODL free of cost during life time of meter. The bidder should provide DLMS compliance for Communication with the meter through Optical port. Bidder should also provide protocol / API for hosting in smart modem using GPRS / RF technology for capturing full data / partial data from the meter and sending it to server / HES OTA. | Meter is complaint to DLMS | ok
69 | 4.1.6 | Bidder should also provide software for changing firmware of meters in mass. Any software / keys required to reprogram the meter and any other support for enabling TPNODL to execute this option will be provided without any additional cost to TPNODL. | Firmware upgarade provision not available as per IS 15959 part 1. | As per our sepecification
70 | 4.2.1 | Magnetic Field: Meter shall record accurate energy in case of any external influencing signals in line with IS 14697:1999 Cl.11.2 and variation in limits of error (upto 100% Imax) shall be as per the table 13 of IS 14697. Meter shall be immune to any magnetic field such that it shall not affect the normal overall functionality However, in case of abnormal magnetic field as defined below meter shall perform as per the following actions: a. Meter shall log the event in its memory as” Magnet” with date and time stamp along with snapshot and the event logging threshold values as per table no. 1 in 4.4 b. The energy recording to shift on I max, Vref. with UPF. Abnormal Magnetic field is defined as below: a. Continuous DC magnetic induction: >0.20 Tesla ± 5% (Value of the magneto motive force to be applied shall be generally >10000 AT. b. AC magnetic induction: >10 milli Tesla ( if produced with circular metal core with square cross section as specified in CBIP latest report with 2800 AT) c. Permanent Magnet: Immune up to 0.5T and Event logging >0.5T. | Meter is immune to Magnetic tests as defined in CBIP 325 and IS14697. Meter is immune to 0.5T. | As per our sepecification
71 | 4.2.4 | Meter should immune to high/low frequency jammer devices. Meter shall log the event in its memory as” JAMMER” with date and time stamp along with snapshot, the threshold values as per table no. 1 in 4.4. | Jammer device performance is not gurataneed, Meter is immune for Jammer device available with MPS. Logging can't be provided. | As per our sepecification
72 | 4.2.5 | The meter should be immune or log the tamper on application of any other higher magnetic field of any frequency waves, micro waves like magnetron etc. the threshold values as per table no. 1 in 4.4. | Meters are not tested with magnetron and performance is not guranteed. Meters to be sent to TPNODL lab and to be tested for performance. | As per our sepecification
73 | 4.3.2 | The meter shall not saturate on passage of direct current, which can cause the meter either to stop recording/ record inaccurately. DC injection shall be tested both in phase and neutral. Measurement by meter shall not get influenced by injection of Chopped signal/ DC signal/ DC pulse upto 330V (both + & - DC) and for any value beyond this, of any low frequency and harmonics. Meter shall log the event into memory as ‘Neutral Disturbance’ with date & time stamp the thresholds are as per table no. 1 in clause 4.4 below. | Meter is immune to Chopped Signal/DC Signal/DC pulse in balalced load condition. Logging can’t be provided. | As per our sepecification
74 | 4.4.4 | Multiple occurrences of same event, with different time stamps should not be logged without restoration of first occurrence, except for the case of Top Cover Open. | Please clarify whether,Cover open multiple occurecne required. | As per our sepecification
75 | Table No 1 | ESD/JAMMER = immediate (record only 1 event on first application & only one event for next 1min) (ESD) | Logging can't be provided. | As per our sepecification
76 | Table No 1 | Microwave - immediate (record only 1 event on first application & only one event for next 1min ) | Logging can't be provided. Design is not validated against microwave and performance is not guranteed | As per our sepecification
77 | 4.4.7 | The meters are to be used for registration of energy consumed by the consumer, as such the meters shall be programmed for import mode and in case of reversal of energy direction (reversal of all CT terminals) meter shall register energy separately in export mode i.e. in case of CT reversal, meter shall record scalar (not vector sum) sum of energy. The meter shall accurately distinguish between actual CT reversal and condition due to faulty reactive power compensation devices/ capacitor banks. Appropriate logics for the same shall be provided in meter. | We understand that in case of one or two phase CT reversal in Unidirection mode Energy recording should be F = F+R and R = 0 ,please confirm. Also Please confirm what should be Enrgy logic if all 3 phases are reversed. | As per our sepecification
78 | 4.4.6 | The meter shall register correctly if supply neutral is not available at the meter neutral terminal. The meter shall work in absence of any two incoming wires. It shall keep recording correctly in case of unbalance system voltage also as defined above. | Accuracy is not guranteed during unbalance voltage condition. | As per our sepecification
79 | 5.2.7 | Temperature sensor to be for sensing the temperature and meter should be programmed in such way that on reaching the threshold value set (as per tamper table no. 1) the event must get logged. | Only controller DIE temperature measurement can be proivded. Threshold level required. | ok
80 | 5.2.8 | Internal diameter of the terminal holes shall be minimum 5 mm; minimum clearance between adjacent terminals shall be 10 mm. Minimum Depth of the terminal holes shall be of 20 mm. | Diameter : 5.5mm +/-0.2 mm Depth: 15 mm +/- 0.5 mm | ok
81 | 5.2.11 | Meter terminal should have 10 terminals arrangement. The terminals should have center to center distance of min. 11.5mm. Terminal configuration shall be R-Cin, R volt, R-Cout, Y-Cin, Y volt, Y-Cout, B-Cin, B-volt, B-Cout, Neutral. | Standard SEIPL terminal arrangement will be provided. Voltage in the top row and current in bottom row. | ok
82 | 5.3.4 | The terminal cover should open on the top side, during connection of the cables. The side opening of terminal cover is not acceptable due to additional opening space requirement. | Terminal cover will be hinged on left side as per the existing design & shall opened from right to left | As per our sepecification
83 | 5.7.1 | Load survey (for pre-paid & post- paid meter mode) Meter serial number shall be recorded and communicated for all profiles of data. The meter shall be capable of recording 30 minutes average of the following parameters for at least last 90 days a) Voltage for each phase b) Current of each phase c) Average PF d) Average kWh e) Average kVAh (lag only) f) kVArh(Lagging) g) kVArh(Leading) h) Temperature near terminal block (˚C) i) THD Voltage phase wise j) THD Current phase wise | h) Temperature near terminal block can’t be provided.Only DIE temperature can be provided. | As per our sepecification
84 | For all line items TYPE TEST CERTIFICATE | The bidder shall furnish the type test certificates of the same design of offered in bid meters for the tests as mentioned above as per the corresponding standards. All the tests shall be conducted at CPRI / ERDA / UL as per the relevant standards | we request you to kindly also accept Type Test Reports of any NABL Accredited Laboratory. | As per our sepecification

## HT CONSUMER METER
Format for Technical Pre-Bid Queries
Tender No: TPNODL / OT/ 2021-22/066
Package Name : HT Consumer meter
Sr. No. | Detailed Reference to Tata Power Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | Tata Power Response
1 | 2 | 3 | 4 | 5
1 | Clause no. 4.01 | Clause No. 4.01 Three Phase Four Wire, AC Static Current Transformer (CT) and Voltage Transformer (VT) operated Watthour and Var-hour Energy Meter. It consists of measuring elements(s), time of use of register(s) and display and plug in type bi-directional communication module all integral within the meter housing. The meter design shall be such that only CT MF is required energy calculation. | We understand that the requirement of plug in type bi-directional communication module all integral within the meter housing is not in the scope of this tender. Request you to please amend the same. | ok
2 | Clause no. 4.03 Annexure-I | Clause No. 4.03 a. For 11kV – Ib = 1A; Imax= 10 Amps (Balanced and Unbalanced Load) b. For 33/66kV/220kV – Ib shall be 1A (shall be defined in tender) When Ib= 1A; Imax= 2 Amps (Balanced and Unbalanced Load) | Please confirm the requirement- Offered meter have two variant 1) Ib = 1A; Imax= 2 Amps 2) Ib = 5A; Imax= 10 Amps Please confirm the same for requirement of 11 KV rating Please accept the same. | ok
3 | Clause no. 4 Annexure-I Unbreakable, high grade, fire retardant reinforced Insulating material (protective Class II) with FV0 Fire Retardant, self - extinguishing, UV stabilize, recyclable and Anti oxidation properties | Clause No. 4.15 Resistance to heat and fire The terminal block and Meter case shall ensure safety against the spread of fire. They shall not be ignited by thermal overload of live parts in contact with them as per clause 6.8 of IS 14697 fire retardant material shall be used. | Terminal block is most important part as it undergoes thermal stresses due to over current/heating. Our meter’s terminal block is V0 compliant plastic. Meter enclosure and terminal cover are made of LEXAN 143 or equivalent material FV2 Compliant. It has to be noted that over current related heating affects the terminal block most. Not the meter cover or terminal cover. Same should be acceptable | ok
4 | Clause no. 4 | Clause No. 4.23 Self-Diagnostic feature The meter shall have logging with date and time in memory for un satisfactory / non-functioning of 1. Real Time Clock 2. RTC battery 3. Non Volatile Memory | Status of RTC & NVM will be available on meter display under “self diagnostic “display parameter. Also in case of NVM & RTC failure meter will log the same as event along with date & time. Status of RTC & NVM not available at BCS ends in healthy condition. Self diagnostic will be available on Display only, as describe below:- Self diagnostic check 00: Healthy, 01: NVM Fail, 02: Battery Fail, 03: Both Fail Same should be acceptable. | ok
5 | Clause No 4.26 Annexure-I serial no. 2 Depth of terminal hole :20 | Clause No 4.26 Internal diameter of the terminal holes 5 mm ( minimum ) Depth of the terminal holes 20 mm (minimum) Annexure-I serial no. 2 Depth of terminal hole :20 | Depth of the terminal holes is approx.. 18 mm. Please accept the same. | ok
6 | Clause no. 4 | Clause no. 4 4.29 Display a. Backlit LCD, Scrolling, 10 seconds for each Parameter minimum 8 digits LCD display. | In offered meter, 7 segment 7 digit displays will be provided. Same should be acceptable. | ok
7 | Clause no. 4 | Clause No 4.30 Software and communication compatibility The bidder shall supply software required for communication through MRI and BCS software including required training to use the software free of cost. The meter shall be compatible to communicate with GSM/GPRS/RF modems in DLMS protocol. | Offered meter comply as per IS: 15959. The meter will have facility to data transfer locally through CMRI and remotely through GSM/GPRS Modem only as per DLMS protocol. We understand that supply of external modem is not in the scope of this tender. Please confirm the same. | ok
8 | Clause no. 4 | Clause No 4.34 Harmonics recording The meter should record the current and voltage THD. The meter should record harmonics up to 20th harmonic Average THD of all phase for voltage THD and current THD. THD values shall have 30/15 minutes (as applicable) integration period in load survey. Accuracy of harmonics recording shall be as per meter accuracy class. The meter shall generate a flag whenever the threshold (user configurable) of the 5% THD of the load current and voltage is breached. | In offered meter, THD voltage event & THD current event is available, limit will be factory configurable only. Same will not available in load survey. Limits for measurement & logging of THD Voltage & current is available in event logging. However meter also have display parameter to show phase wise voltage , current & power THD. THD is not supported in load survey. | ok
9 | Clause no. 4 | Clause No. 4 4.1 Software & communication capability: The meter shall be compatible to communicate with GSM/GPRS/RF modems in DLMS protocol. Clause No. 4.1. Communication capabilities and software feasibilities: 4.1.1 The meter shall have facilities for data transfer locally through MRI (Using optical port/RJ11/RF modems) and remotely using optical port/RJ11 port via GSM/GPRS/RF modems with proper security through optically isolated ports through serial communication. 4.1.2 Meter should have additional RJ11/ RJ45 port to communicate with GSM/GPRS/RF modems. 4.1.5 Bidder should also provide protocol / API for hosting in smart modem using GPRS / RF technology for capturing full data / partial data from the meter and sending it to server / HES OTA. | Offered meter comply as per IS: 15959. The meter will have facility to data transfer locally through CMRI and remotely through GSM/GPRS Modem. We understand that supply of external modem is not in the scope of this tender. Please confirm the same. | ok
10 | Clause no. 4.1 | Clause No. 4.1 Communication capabilities and software feasibilities: 4.1.6. Bidder should provide software for changing firmware of meters in mass. Any software/keys required to reprogram the meter and any other support for enabling TPNODL to execute option will be provided without any additional cost to TPNODL. 4.1.9 Bidder to supply protocol to read the meters supplied against this tender using intelligent RF/GPRS/GSM modem with store and forward feature without any additional cost implication. Bidder to provide API on MIOS standard to convert the meter data in to XML and read API for hosting in server and modem RF/GSM/GPRS based for reading meters from any third party manufactured modems. Bidder to provide necessary support if required during integration of the RF modem with supplied meters against this tender. | Offered meter comply as per IS: 15959. We do not recommend firmware change of the meter however meter configuration changes allowed by IS 15969 are possible, e.g. TOD, Billing date etc. We will provide windows based common meter reading API for meter reading which will run at head end system and perform in transparent mode. We will provide MIOS based XML file of meter data, However integration is not in our scope. Please confirm the same. | As per our specification
11 | Clause no. 4.2 | Clause: 4.2.1 Magnetic field : Meter shall be immune to magnetic field such that it shall not affect the normal overall functionality however, in case of abnormal magnetic field as defined below meter shall perform as per the following actions: a) Meter shall log the event in its memory as “MAGNET” with snapshot and the event logging threshold values as per table no. 1 in 4.4 b) The energy recording to shift on Imax, Vref with UPF. | Meter with compliance to CBIP 325 for influence of magnetic induction shall also be acceptable. Meter would be immune and within permissible accuracy limits as per CBIP 325 and if meter gets affected it will log magnetic event with date and time and start recording at I Max. Magnet P time for occurrence & restoration shall be 20-30 secs approx. to avoid tampering through any timer based tampering methods. Specific Legend will be available on LCD of meter as below:- Suitable abbreviation/information will also provided under “present status other then CT & PT related events”. Display parameter. Same should be acceptable. | As per our specification
12 | Clause no. 4.2 | Clause: 4.2.1 Magnetic field : Abnormal magnetic field is defined as below: a) Continuous DC magnetic induction: >0.20 Tesla±5% (value of the magneto motive force to be applied shall be generally>10000 AT) | Meter will compliance to CBIP 325 for influence of magnetic induction will also be acceptable. Immunity level up to 0.5 T & 0.2Tis not guaranteed; Either Meter would be immune and if meter gets affected it will log magnetic event with date and time and start recording at I Max. Specific Legend will be available on LCD of meter | As per our specification
|  | Clause: 4.2.1 Magnetic field : Abnormal magnetic field is defined as below: b) AC magnetic induction: >10 mili Tesla (if produced with circular metal core with square cross section as specified in CBIP latest report with 2800 AT) |  | As per our specification
|  | Clause: 4.2.1 Magnetic field : Abnormal magnetic field is defined as below: c) Permanent magnet: Immune up to 0.5T and event logging> 0.5T |  | As per our specification
13 | Clause no. 4.2 | Clause: 4.2.2 Electrostatic Discharge (ESD) Meter shall be immune up to 50KV and shall record accurate energy as per IS: 13779:1999/CBIP 325. Meter shall log the event into memory as ESD with date and time stamp for any ESD greater than 50KV with snapshot, the event logging threshold values as per table 1 in 4.4. | Offered meter will be immune under influence of spark up to 35KV. However the meter immune up to certain high level of spark. “Abnormal external interference” event with date and time stamp will indicate ESD tampering. Offered meter is as per previous supplies, it is kindly requested to accept the same. | As per our specification
14 | Clause no. 4.2 | Clause: 4.2.4 Meter should be immune to high/low frequency devices. Meter shall log the event in its memory as “Jammer” with date and time stamp with snapshot, the threshold values as per table no. 1 in 4.4. | Against any external interference devices offered meter will complies as per IS 13779 & CBIP 325. “ Meter will be immune to high/low frequency. If it gets affected, it will log event “abnormal external interference. | As per our specification
15 | Clause no. 4.2 | lause No. 4.2.5 The meter should be immune or log the tamper on application of any other higher magnetic field of any frequency waves, micro waves like magnetron etc. | This is very specified & non standard requirement under such influence meter may behave abnormally, it may be immune or permanently damage Offered meter will complies as per IS 13779 & CBIP 325. If it gets affected, it will log event “abnormal external interference. | As per our specification
16 | Clause no. 4.3 | Clause 4.3.2 4.3.2 The meter shall not saturate on passage of direct current, which can cause the meter either to stop recording/ record inaccurately. DC injection shall be tested both in phase and neutral. Measurement by meter shall not get influenced by injection of Chopped signal/ DC signal/ DC pulse upto 330V and for any value beyond this. Meter shall log the event into memory as ‘Neutral Disturbance’ with date & time stamp the thresholds are as per table no. 1 in 4.4 | Meter will remains either immune or if it gets affected metering functionality log ND event & record energy at V-ref X Actual current X UPF. Accuracy will be ±4%. Specific Legend can be provided on LCD of meter Offered meter is as per previous supplies, it is kindly requested to accept the same. | As per our specification
17 | Clause no. 4.4 | Clause No. 4.4.1 The meter shall record forward energy under all abnormal tampering conditions and shall be capable of recording occurrence and restoration of abnormal events listed below along with the date and time and snapshot of individual voltages, current, power factors, active energy and apparent energy at the time of occurrence of abnormal event and restoration of normal supply. | Events will log as per prevailing electrical conditions. Offered meter have event logging as per IS: 15959. However if case meter record tamper, it will log snap shot on confirmation of event i.e. either occurrence or restoration. Considering restoration & occurrence events as separate event. Snap shot will be Voltage, Line current, Neutral current & configured energy. It is kindly requested to accept the same | As per our specification
18 | Clause no. 4.4 | Clause No. 4.4.2 The time stamp and snapshot parameters shall be recorded at the start time of event of occurrence (T1) and for restoration the time stamp and snapshot parameters shall be recorded at the end time of the event (T3). | Offered meter have event logging as per IS: 15959. However if case meter record tamper, it will log snap shot on confirmation of event i.e. either occurrence or restoration (after Persistence –time). Snap shot will be Voltage, Line current, Neutral current & configured energy. | As per our specification
19 | Clause no. 4.4 | 4.4.4 Multiple occurrences of same event, with different time stamps should not be logged without restoration of first occurrence, except for the case of Top Cover Open. | Offered meter have event logging as per IS: 15959. The tamper events will be stored in relevant compartment (i.e. All voltage related event will be logged in one compartment) on FIFO basis limited to no. of event assigned to that compartment. Occurrence & restoration event consider as separate event. So availability of unrestored/restored events details will depends upon nos. of tamper events assigned to relevant compartment. | As per our specification
20 | Clause no. 4.4 | Clause no. 4.4.7 The meter shall record in export registers in case of reversal of all CT terminals. The meters are to be used for registration of energy consumed by the consumer, as such the meters shall be programmed for import mode and in case of reversal of energy direction (reversal of all CT terminals) meter shall register energy separately in export mode i.e. in case of CT reversal, meter shall record scalar (not vector sum) sum of energy. | The meter will record in forward direction in case of reversal of all CT terminals. In case of one, two or all three CT reversal offered meter will register energy in Active export under CT reverse register along with the forwarded energy register. | As per our specification
21 | Clause no. 4.4 | Clause no. 4.4.8 The meter shall register correctly if supply neutral is not available at the meter neutral terminal. The meter shall work in absence of any two incoming wires. It shall keep recording correctly in case of unbalance system voltage also as defined above. | Meter will record energy & event as per prevailing electrical conditions | ok
22 | Clause no. 4.5 | Clause 4.5 Event Compartments | The tamper events will be logged in their respective compartment as per IS15959:- 1) Voltage related event -150 Nos. 2) Current related events – 150 Nos. 3) Other Events -150 Nos. 4) Non roll over – Cover open (5 nos.) 5) Power failure – 50 Nos. Occurrence event and restoration event taken as separate event. Same should be acceptable. | ok
23 | Clause no. 4.5 Annexure-I serial no. 4 | Clause 5.0 General constructions Battery: Guaranteed life of 15 years Annexure-I serial no. 4 Battery: Guaranteed life of 15 years | Operating life of battery would be 10 years. | ok
24 | Clause no. 5.10 Annexure-I serial no. 1 | Clause 5.1 Meter Body 5.1.1 The meter body shall be made of unbreakable, high grade, fire retardant, reinforced insulating material (protective class II) with FV0 Fire retardant, self extinguishing, UV stabilize, recyclable and anti oxidation properties. 5.1.3 Meter base shall be opaque with polycarbonate LEXAN 500R or equivalent on prior approval from TPNODL. 5.1.4 Meter cover shall be transparent with polycarbonate LEXAN 143R/943A or equivalent on prior approval from TPNODL. Annexure-I serial no. 1 a) Base: Opaque with polycarbonate LEXAN 500R or equivalent b) Cover: Transparent with polycarbonate LEXAN 143R/943A or equivalent | The meter case cover & base and ETBC will be FV2 Compliant & Meter terminal will be FV0 compliant. Offered meter have opaque meter base & terminal block and transparent meter cover. However material will be: Meter case base & cover: LEXAN 143 or Equivalent Terminal Block: LEXAN 500R/equivalent | ok
25 | Clause no. 5.1 Annexure-I serial no. 1 | Clause 5.1 Meter Body 5.1.2 The minimum thickness of the meter enclosure shall be 2mm. Annexure-I serial no. 1 Thickness, Min. 2.0 mm | Thickness will be approx 2mm ± 0.2mm. | ok
26 | Clause no. 5.2 Annexure-I serial no. 2 | Clause no 5.2.3 Terminal block and terminal cover shall be of a material which complies with the requirements of IS11731 (part 1) method FH1. The material of which the terminal block is made shall be capable of passing the Heat Deflection temperature test given in ISO 75 for temperature of 135°C and pressure of 1.8 MPa as mentioned in IS 14697. Tested as per ISO 75-2/A or ASTM D648. Terminal block and terminal cover shall be of a material which complies with the requirements of IS11731 (part 1) method FH1. The material of which the terminal block is made shall be capable of passing the Heat Deflection temperature test given in ISO 75 for temperature of 135°C and pressure of 1.8 MPa as mentioned in IS 14697. Tested as per ISO 75-2/A or ASTM D648 | Only Terminal block is most important part as it undergoes thermal stresses due to overcurrent/heating. Complies with HDT limit of 135 deg C should only applicable for terminal block . Same should n't be mandatory for terminal cover . | ok
27 | Clause no. 5.2 | Clause no. 5.2.7 Temperature sensor to be for sensing the temperature and meter should be programmed in such way that on reaching the threshold value set (as per tamper table no. 1) the event must get logged. | As per IS 15959 Temperature rise event is not defined, hence same is not provided. | As per our specification
28 | Clause No. 5.1/ | Clause No. 5.3 Terminal cover 5.3.1 Terminal cover will be short type & transparent with virgin polycarbonate LEXAN 143A/943 or equivalent material. 5.3.2 The terminal cover should be of short type 20 to 25mm length 5.3.5 The terminal cover design should be such that sealing screw locking provision on cover should have min dimension of 3mmx3mm (excluding seal lock hole) | Terminal cover will be transparent with polycarbonate LEXAN 143A/943 or equivalent material. Terminal cover will be extended type & ETBC to Terminal bottom will be approx 40-45mm. In offered meter, Suitable arrangement will be provided. Sealing holes on sealing screw is sufficient to accommodate lash wire of seal However hole dia will be approx 2mm | ok
29 | Clause No. 5.6 | Clause no. 5.6 MD Integration: The MD integration period shall be 30/15 minutes (integration period-programmable by CMRI at site and also thru AMR with adequate security level). The MD resetting shall be automatic at the 1st of the month i.e. 0000 hours of 1st day of the month. Manual MD reset button shall not be available. Last 12 MD values shall be stored in the memory. MD shall be recorded and displayed with minimum three digits before decimal and minimum two digits after decimal points. MD integration shall be of sliding Type at an interval of 10 min. | Sliding window internal will be 1/3 rd of DIP. I am requesting you please amend accordingly, we are providing better option. | ok
30 | Clause No. 5.7 | Clause no. 5.7 Parameters in BCS All these parameters (mention below clauses) shall be downloaded locally or remotely and interpreted in PC/Laptop. | For remote external modem will required, however, we understand modem is not in our scope. | ok
31 | Clause No. 5.7.1 | Clause 5.7 Load survey: The meter shall be capable for recording 30 min. average of the following parameters for 60 days: 1)Termperature near terminal blok 2)THD volatge phase wise 3)THD current phase wise | This is very specified requiremen, same shouldn't be mandatory requirement. Limits for measurement & logging of THD Voltage & current is available in event logging. However meter also have display parameter to show phase wise voltage , current & power THD. Same should be acceptable | As per our specification
32 | Clause No. 5.7.1 | Clause 5.7 Load survey: The meter shall be capable for recording 30 min. average of the following parameters for 60 days: 1. Voltage per phase 2. Current per phase 3. Power Factor per phase 4. Average kWh 5. Average KVAH 6. kVArh (lag) 7. kVArh (lead) | Calculated power factor will be available in load survey instead of phase wise power factor. | As per our specification
33 | Clause No. 5.7.2 | Clause No. 5.7.1 Load survey: Meter shall be capable of recording daily Energy and Demand 00:00 to 24:00 Hrs kWh/kVAh, kW/kVA in BCS for 90 days. Midnight energy value of cumulative kWh/kVAh and daily consumption kWh/kVAh should be available in meter memory for last 90 days. | Offered meter records cumulative kWh for mid night energy & load survey for 90 days as per IS 15959. User can manually calculate the consumption for configured energy. | As per our specification
34 | Clause No. 5.7.2 | Clause No. 5.7.2 Load survey: Meter shall be capable for following instantaneous parameters in memory and should be available in BCS. Meter date & time DD MM YYYY HH MM SS MRI/PC date & time DD MM YYYY HH MM SS Dump date & time DD MM YYYY HH MM SS | Following parameters will be available:- Meter date & time (dd / mm/ yyyy HH MM SS) & Meter reading date & time (dd /mm/ yyyy HH MM SS) will be available | ok
35 | Clause No. 5.7.2 | Clause No. 5.7.2 Meter shall be capable for following instantaneous parameters in memory and should be available in BCS. Cumulative Power OFF duration 00000 Cumulative Power On duration. 00000 | Cumulative Power OFF duration & Cumulative Power On duration will be available in form of (YY DDD HH MM). | ok
36 | Clause No. 5.7.2 | Clause No. 5.7.2 Meter shall be capable for following instantaneous parameters in memory and should be available in BCS. Terminal block temperature | This is very specified requiremen, same shouldn't be mandatory requirement. Not available in instantaneous parameters. | ok
37 | Clause No. 5.7.2 | Clause No. 5.7.2 Meter shall be capable for following instantaneous parameters in memory and should be available in BCS. Last Billing date dd:mm:yyyy | Not available in instantaneous parameters Billing date will be available in Reading parameter & Average temperature of meter will be available in LS at BCS end | ok
38 | Clause No. 5.7.3 | Clause No.5.7.3 General information Manufacture date (MM/YYYY) TOD Profile profile showin timming and seasons | Manufacturing Year will be available & TOD profile showing timing and seasons are not available. Only TOD profile will be available in TOD data at BCS end | ok
39 | Clause No. 5.7.4 | Clause no. 5.7.4 Billing Parameters TOD details with day time and season wise. | TOD profile showing timing and seasons are not available. Only TOD profile will be available in TOD data at BCS end | ok
40 | Clause No. 5.7.6 | Clause no. 5.7.6 Tamper events The meter should not have any other events logging or any logic other than desired in specs | This is specified requirement, Each & every manufacturer have different specified logics for tamper. Please amend accordingly | ok
41 | Clause No. 5.8 | Clause 5.8 Display units The LCD display shall have a wide viewing angle of 120 degree. The Wh & VAh register shall have minimum 8 digits LCD display and size of the digits shall be minimum 10mmx5mm.Cumulative energy (Wh & VAh) shall be displayed without decimal in auto scroll mode. (However decimal shall be available in push button mode for high resolution display for testing). | It is requested to accept viewing angle of minimum 60 degree. 7 digit display with digit size of 10mm x 5 mm Resolution for energy, demand will depends upon commissioning of meter. | ok
42 | Clause No. 5.8.1 | Clause No. 5.8.1 Push mode: ESD tamper count Latest ESD tamper occurrence date Latest ESD tamper occurrence time TC Open occurrence date of very first event TC Open occurrence time of very first event Last Magnet tamper occurrence date Last Magnet tamper occurrence time | Offered meter will be immune up to 35KV spark and HV as per relevant standard. Tamper details will be available in following display parameters: • Present status of CT events • Present status of PT related events • Present status other then CT & PT related events • First occurred tamper • Date of first occurred tamper • Time of first occurred tamper • Last occurred tamper • Date of last occurred tamper • Time of last occurred tamper • Last restored tamper • Date of Last restored tamper • Date of Last restored tamper •TC Open occurrence date of last event •TC Open occurrence time of last event Suitable information /abbreviation will be provided at display under” Present status other then PT & CT”. Same should be acceptable | ok
43 | Clause No. 6 | Clause 6.0 Name plate and marking The base color of name plate shall be blue (as of TPC) | Rating plate information’s will be laser printed on rating plate as per IS: 1497. Base of rating plate will be off white & character will black in color It will be same as previous supply of Tata power. | ok
44 | Clause No. 6 | However the following shall be printed in bar code on the meter nameplate (shall be laser printed on name plate instead of any sticker). All data shall be laser printed on meter along with Sr.NO and date of manufacturing. No sticker to be used to avoid loss of data in event of fire. Content Format for bar code: TPNODL MMYY XXXXXXXX (8-digit Serial no.). The PCB Serial number should be printed on the PCB instead of sticker. | The meter will have manufacturer specific 8 alpha-numeric digit serial no. & Barcode will contain manufacturer specified meter Sr. Nos. only (laser printed). All other information will be laser printed on rating plate. Same should be acceptable. | ok
45 | Clause No. 7.3 | Clause 7.3 Acceptance test | Acceptance test will be performed as per IS 14697 | ok
46 | Clause No. 7.5 | Clause 7.4 Special Test: The bidder shall ensure that API is compatible with TPC’s CFW. | Offered meter comply as per IS: 15959. Open protocol Same as per previous supply | ok
47 | Clause No. 9 | Clause No. 9.0 i)1 no. leaflet with each meter | Same will be provided in softcopy. | As per our specification
48 | Clause No. 8 | Clause No. 8 Type Test Certificate: All the tests shall be conducted at the CPRI/ERDA as per relevant standard. | Type Test should be conducted in NABL Certified test Laboratory. We have type test report form NABL accredited lab (YMPL). Kindly accept the same. | As per our specification
49 | Clause No. 11 | Clause No. 11 Guarantee Bidder shall be further be responsible for free replacement at site for another period of Three years from the end of the guarantee period for any latent defects if noticed and reported by the TPC. | Offered meters will be guaranteed for a period for 5 years from the date of supply. No additional
50 | Clause No. 12 | Clause no. 12 PACKING 2. Individual meter should be packed in separate box. Routine test report (with manufacturing company logo) of the individual meter shall be kept inside each card board carton of the meter. | Packing will be as per previous supply for Tata power. | ok
51 | Clause No. 12 | Clause no. 12 PACKING On back side of routine test certificate (RTC) the bidder shall print a picture of the meter with its small details like for consumer to know about meter. | Serial no. of meter will be provided in Routine test certificate, Picture of meter will not provided. | As per our specification
52 | Clause No. 13 | Tendering stage: Bidders are required to manufacture 03 numbers of sample meters as per the TPNODL specification (sealed, unsealed and open able base and cover to view/test the inner circuits) and submit the samples (non-returnable) along with bid for approval. These samples should be submitted at TPNODL store. | We are requesting please waive off the sample requirement, as we are regular supplier of Tata power | As per our specification
53 | Clause No. 14 | Clause No. 14 Quality Control Prior to final testing and calibration, sample meters shall be subjected to aging test (i.e. meters will be kept in ovens for 24 hours at 55 Deg. C temperature and atmospheric humidity under real-life condition at its full load current. After 24 hours meter should work satisfactorily. | This test is not performs at our works. | As per our specification
54 | Clause No. 18 | Clause no. 18. Spares, accessories & tools 1. Bidder to be provides free of cost 02 nos of jig for retrieving data from memory of the meter with every new design of the meter in which previous jig is supplied cannot be used. Jig should be such that NVM can be push fit on this jig & data can be retrieving from this NVM. | No JIG will be provided. If required data can be retrieved at our works. | As per our specification
55 | Clause No. 18 | Clause no. 17 Spares, accessories & tools Five (5) nos. of optical cord against each 100 meter lot for retrieving the data of meter through optical port should be provided, if design of optical port is changed from those of previously supplied meters. | Please provide about communication required:- • Optical to DB( male) • Optical to USB Please confirm & amend accordingly | Optical to USB
56 | Annexure-I Inspection test plan | Serial no. 17 All tests as defined in IS 15959 (Part- 2):2011 | It seems there is tophography error, IS15959 part:-1 is applicable for Smart WC meter. Please clarify & ammed accordingly. It should be IS15959 part-1 | ok
57 | Annexure-I Inspection test plan | Serial no.18Communication between Meter and MRI; MRI & BCS Software:-IS16444 Part2 | It seems there is tophography error, IS16444 part:-2 is applicable for Smart meter. Please clarify & ammed accordingly. It should be IS14697 | ok

## HT NET METER
Tender No: TPNODL / OT/ 2021-22/066
HT NET meter
Sr. No. | Detailed Reference to Tata Power Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | Tata Power Response
1 | 2 | 3 | 4 | 5
1 | Clause No. 2 | Clause No. 2 Applicable Standard | IS 13779 is not applicable for CT-PT operated meters. Kindly amend the same. | ok
2 | Clause No. 2 | Clause No. 2 Applicable Standard CBIP 304 | It should be CBIP325 | ok
3 | Clause No. 3.10 | Clause No. 3.10 Billing Data: In Display Parameters Cumulative kVAH and kVArh (import and export). | It seems that there is topography error The Offered meter will be provided with Cumulative kVAH (import and export). It is requested to accept the same. | ok
4 | Clause No. 3.14 Clause No. 3.15 | Clause No. 3.14 Load survey: 15 parameters with 30 days Clause No. 3.15 Time Required for data reading from meter and downloading on desktop PC: Meter Data Consisting of all Parameter and 60 days load survey and load survey parameter read by CMRI downloaded on desktop PC. | Load survey for 30 days as specified in clause 3.14 is required. Please clarify & amend accordingly. | As per our specification
5 | Clause No. 3.18 | Clause No. 3.18 Additional Communication Port: An additional RS232 hardwired port to be provided in terminal block outside in terminal cover for AMR GSM/GPRS to the main computer. | An additional RS232 hardwired port to be provided in terminal block inside terminal cover for AMR GSM/GPRS to the main computer. Kindly accept the same. We understand that supply of external modem is not in the scope of this tender. | ok
6 | Clause No. 3.18 | Clause No. 3.18 Additional Communication Port: f) Bidder shall provide read & convert API on standard and also integrate communication with TPDDL system | The offered meter is on DLMS protocol as per IS 15959 hence API is not required. | ok
7 | Clause No. 4 | Clause No. 4. Body of Meter: 1. Top transparent and base opaque material polycarbonate of Lexan 143A grade. | It is Provided with Lexan 143. It is requested to accept the same. | ok
8 | Clause No. 4.3 | Clause No. 4.3 Terminal cover: The Terminal Cover shall be of short type and shall be transparent with polycarbonate LEXAN 143R/943A or equivalent on prior approval of the purchaser. | It is Provided with Lexan 143. It is requested to accept the same. | ok
9 | Clause No. 4.2 | Clause No. 4.2 Terminal Block: Made of polycarbonate of grade 500 R or equivalent grade and shall form Integral part of the meter base, brass terminal inserts & MS screws. | Offered meter have Ni plated brass terminals with flat-head nickel plated brass screws will be provided | ok
10 | Clause No. 4.4 | Diagram of connections: Diagram of external connections to be shown on terminal cover from inside. | Diagram of external connections will be shown on the inner side of terminal cover | ok
11 | Clause No. 5 | Clause No. 5 Tamper and Anti fraud detection evidence features: Total No. of temper events logged by the meter shall be atleast 200nos. Compartment wise division of each event and their Persistence time indicated in tamper logic list. | Compartment wise tamper events will be provided as per comments provided in clause no. 5.16. | ok
12 | Clause no. 5.3 | Power On / off: - Meter shall detect power OFF (minimum power off period 5 mins). This event shall be recorded at the time of each power OFF. At the same time power ON event shall be recorded. This logging shall be available in Tamper details along with cumulative time of failure. Meter should have provision to record last 100 such events minimum. | Offered meter will have Power Off event logging in case all the three phase are not available. | ok
13 | Clause No. 5.2 | Clause No. 5.2 Detection of missing Potential: The threshold of the voltage should be programmable. | The threshold of the meters will be factory programmable. It is requested to accept the same. | ok
14 | Clause no. 5.4 |  Snap shots: Meter shall log all three-phase voltage, current (line, active and reactive), Reading (Active and Apparent), power factor etc. at the time of tamper attempt for all such occurrences | Offered meter have event logging as per IS: 15959. However if case meter record tamper, it will log snap shot all three-phase voltage, current, power factor, neutral current etc.on confirmation of event i.e. either occurrence or restoration (after Persistence –time) | ok
15 | Clause No. 5.6 | External Magnetic tamper: Meter should log on the events of attempt of tampering by external magnetic field & should function as mentioned in the CBIP Technical report no. 88 with latest amendments. | Meter would log on the events of attempt of tampering by external magnetic field as mentioned in the relevant IS. The Meter will record as per actual load once the external abnormal magnetic field is removed. In such conditions the Meter will log the event for presence of abnormal external magnetic field and its restoration | ok
16 | Clause No. 5.6 | Clause No. 5.6 Over Load: Meter shall Record overload as an event in terms of defined %threshold value of the load (programmable at the factory). | We understand that overload events are required for DT application meters. Hence please accept the meter with over current event configuration, | ok
17 | Clause no. 5.10 | Clause No. 5.10 Protection against HV Spark: Meter should be Immune to spark strength upto 35kV and above and it should record an event (occurrence and restoration) with date and time stamped. | Offered meter will be immune under influence of spark up to 35KV. However the meter immune up to certain high level of spark. “Abnormal interference” event with date and time stamp will indicate ESD tampering. Offered meter is as per previous supplies, it is kindly requested to accept the same. | ok
18 | Clause No. 5.16 | Clause No. 5.16 Abnormal and Tamper Conditions: 1)Meter shall be capable of recording occurrence and restoration of abnormal events with date and time stamped and snapshot for events such as individual voltage, current, power factor, active energy and apparent energy for export and import mode at the time of occurrence and restoration. 2)During Abnormal condition or tamper event the current shall be recorded as active current and line current. | (1.) Snap shot of only 3 energy is provided. So out of below 4 energy any 3 energy can be provided in snap shot:- 1. Active energy Import 2. Active energy Export 3. Apparent energy Import 4. Apparent energy Export It is requested to accept the same. (2.) Line current will be Provided. | As per our specification
19 | Clause No. 5.16. | 1 Abnormal and Temper Conditions: 1 PT MISSING No. of event to be logged=50 2 .HIGH Voltage No. of event to be logged=25 c. Voltage Unbalance No. of event to be logged=50 | Cumulative 125 Nos. voltage retaled Events (occurrence + restoration) will be provided for this compartment, it will not be separate for each event. Events will be logged on FIFO basis. Kindly accept the same. | ok
|  | 2 Abnormal and Temper Conditions: 3 CT Open No. of event to be logged=50 CT Bypass No. of event to be logged=50 Over current No. of event to be logged=25 Current imbalance No. of event to be logged=25 | Cumulative 150 Nos. current related events (occurrence + restoration) will be provided for this compartment, it will not separate for each event. Events will be logged on FIFO basis.Kindly accept the same. | ok
|  | 3 Abnormal and Temper Conditions: Neutral Disturbance No. of event to be logged=25 Magnet No. of event to be logged=25 Low Power Factor No. of event to be logged=25 HV ESD No. of event to be logged=25 | 100 Nos. event will be provided for the events related to abnormal events compartment for ND , magnet & Low Power factor. | ok
20 | Clause No. 5.16.1 | Clause No. 5.16.1 Abnormal and Temper Conditions PT Missing: Threshold value of restoration event: Voltage > 80% of Vref and current > 2% of Ib. | For restoration of PT missing no check of current limit is provided. | As per our specification
21 | Clause No. 5.16.1 | Clause No. 5.16.1 Abnormal and Temper Conditions Voltage Unbalance: 1. Threshold value of restoration event: Shall be less than 10 between the phases and currents should be > 2% of Ib. 2. Threshold value of occurrence event: 20% or more between the phases and current > 2% of Ib | 1. Restoration limit of voltage unbalance is <20%. No check of Current limit is provided for voltage unbalance event. 2. No check of Current limit is provided for voltage unbalance event | As per our specification
22 | Clause No. 5.16.1 | Abnormal and Temper Conditions CT Open: Threshold value of restoration event: Ir + Iy + Ib + In < 5% of Ibasic. Phase current > 10% of Ibasic with all current positive. | Restoration of CT open tamper is provided when the Residual current is <10% and the Average line current >10% of Ibasic. It is requested to accept the same. | As per our specification
23 | Clause No. 5.16.1 | Clause No. 5.16.1 Abnormal and Temper Conditions CT Bypass: 1. Threshold value of restoration event: Ir + Iy + Ib + In < 5% of Ibasic. Phase current > 10% of Ibasic with all current positive. 2. Threshold value of occurrence event: Ir+Iy+Ib+In >10% of Ib and phase current>10% of Ib | 1. Restoration of CT ByPass tamper is provided when the Residual current <10% of Ib and when Average line current >10% of Ibasic. 2. Occurrence of CT Bypass event will be provided when phase current >5% of Ib. | As per our specification
24 | Clause No. 5.16.1 | Clause No. 5.16.1 Abnormal and Temper Conditions Overload Current: Threshold value of restoration event: <110% of Imax Threshold value of occurrence event: >125% of Imax | Offered meter will log over current when >125% of Imax & restored when <125% I max . It is requested to accept the same. | As per our specification
25 | Clause No. 5.16.1 | Clause No. 5.16.1 Abnormal and Temper Conditions Neutral Disturbance: Persistence Time of Occurrence: 2 min. Persistence Time of Restoration: 2 min. Threshold value of restoration event: Voltage <110% of Vref, Current>2% of Ib, frequency>47Hz and frequency<52HZ. Threshold value of occurrence event: Voltage <110% of Vref, Current>2% of Ib, frequency>47Hz and frequency<52HZ, dc Voltage/signal injection. | Persistence Time of Occurrence:30 seconds Persistence Time of Restoration: 90 seconds Threshold value of occurrence event: In case of spurious signal injected in neutral of the meter, offered meter will be either immune or if gets affected register energy on reference voltage, actual current and UPF. Meter will have legend for neutral disturbance tamper on LCD display. Threshold value of restoration event: under normal condition i.e without spurious signal. | As per our specification
26 | Clause No. 5.16.1 | Clause No. 5.16.1 Abnormal and Temper Conditions Magnet: Threshold value of restoration event: <0.5 Tesla (permanent magnet).DC Magnet induction <0.20 Tesla. AC Magnet induction <0.15 Tesla. Threshold value of occurrence event: >0.5 Tesla (permanent magnet).DC Magnet induction >0.27 Tesla. AC Magnet induction >0.2 Tesla. | Under influence of external magnetic field offered meter will work as per relevant IS and CBIP 325. Meter will either immune or metering gets affected,meter will log magnet event with date & time & start recording energy at Imax X Vref X UPF. Same should be acceptable | As per our specification
27 | Clause No. 5.16.1 | Clause No. 5.16.1 Abnormal and Temper Conditions Power On-Off: Persistence Time of Restoration: 5 min. | Offered meter will log immediate Power-On OFF event. It is requested to accept the same. | ok
28 | Clause No. 6.4 | Clause No. 6.4 Display Module Makes and Origin: Hongkong: Genda Singapore: Bonafide Technology Ever light Japan: Hitachi, Sony Korea: Advantech China: Success Holland/Korea: Phillips | Hongkong: Genda Singapore: Bonafied Technologies Everlight, Truly semiconductor Korea: Advantek China: Sucess Japan: Hitachi, Sony Holland / Korea: Phillips or any reputed make | ok
29 | Clause No. 6.4 | Communication modules: Communication modules should be compatible for the two RS 232 ports (one for optical port for communication with Meter reading instruments & the other - for the hardwired RS 232 port to communicate with various modems for AMR) | USA: National Semiconductors, HP, Optonica,ST,Everlight Holland / Korea: Phillips Japan: Hitachi Taiwan: Ligitek Germany: Siemens or any reputed make | ok
30 | Clause No. 6.4 | Battery Varta , Tedirum sanyo or national vitzrocell tekcel | Tekcell, SAFT, Varta , Xeno energy, Eve, Panasonic, Mitsubishi or any reputed make same should be acceptable | ok
31 | Clause No. 7.1 | On name plate Manufacturer's code (given by TPNODL) | The meter will have manufacturer specific 8 alpha-numeric digit serial no. & Barcode will contain manufacturer specified meter Sr. Nos. only (laser printed). All other information will be laser printed on rating plate. Same should be acceptable. | ok
32 | Clause no. 7.2 | Clause No. 7.2 1. Bidder shall supply software suitable for energy measurement and energy spot billing through CMRI. 2. Meter Sr. No. shall be printed inside the meter top cover. | 1. In the Offered Meter the Spot billing is not supported. 2. In the offered Meter the Meter Sr. No. is Printed on the rating plate. Kindly accept the same. | ok
33 | Clause no. 9 | 2:Acceptance Test: Regarding Limits of error. 3. Type test:All test as defined in IS13779 | Please ammed all limits are applicable for WC meter only. Please remove & ammend accordingly | ok
34 | Clause no. 10 | Clause No. 9.10 Type Test Certificate: All the tests shall be conducted at the CPRI/ERDA as per relevant standard. | We have type test report from YMPL.Same should be acceptable | As per our specification
35 | clause no. 13 | Guarantee Bidder shall be further be responsible for free replacement at site for another period of Three years from the end of the guarantee period for any latent defects if noticed and reported by the TPC. | Offered meters will be guaranteed for a period for 5 years from the date of supply. No additional
36 | clause no. 14 | PACKING 2. Individual meter should be packed in separate box. Routine test report (with manufacturing company logo) of the individual meter shall be kept inside each card board carton of the meter. | Packing will be as per previous supply for Tata power. | ok
37 | clause no. 16 | Clause No. 16 Quality Control Prior to final testing and calibration, sample meters shall be subjected to aging test (i.e. meters will be kept in ovens for 24 hours at 55 Deg. C temperature and atmospheric humidity under real-life condition at its full load current. After 24 hours meter should work satisfactorily. | This test is not performs at our works. | As per our specification
38 |  | Reverse Auction TPC reserves the right to conduct the reverse auction for the product/ services being asked for in the tender | We will quote our best competitive prices. We will not be able to participate in RA. It is kindly request you to please amend the same. | ok

## LT NET METER
Tender No: TPNODL / OT/ 2021-22/066
LTCT NET meter
Sr. No. | Detailed Reference to Tata Power Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | Tata Power Response
1 | 2 | 3 | 4 | 5
1 | Annexure I : LOT B : | S.No.8) 3-ph,4-wire LTTV Meter,100/5A,0.5 class with BOX(KWH Meter) , S.No.9) 3-ph,4-wire LTTV Meter,150/5A,0.5 class with BOX(KWH Meter) | We understand that supply of LTCT meter is required with 230V Vref. Please confirm if Meter box is required with supply or not. Kindly provide Meter box specification and drawing for reference. | Push fit type meter box is required with CT. Meter Box specification with drawing to be provided.
2 | Clause No. 3.15 | Time Required for data reading from meter and downloading on desktop PC: Meter Data Consisting of all Parameter and 60 days load survey and load survey parameter read by CMRI downloaded on desktop PC. | Load survey for 30 days as specified in clause 3.14 is required. Kindly accept the same. | As per our specification
3 | Clause No. 3.18 Additional Communication Port: | An additional RS232 hardwired port to be provided in terminal block outside in terminal cover for AMR GSM/GPRS to the main computer. | An additional RS232 hardwired port to be provided in terminal block inside terminal cover for AMR GSM/GPRS to the main computer. Kindly accept the same | As per our specification
4 | Clause No. 3.18 | F) Bidder shall provide read and concert API on MIOS standard and also integrate communication with the TPDDL system | Integration will be not covered in our scope. | As per our specification
5 | Clause No. 3.23 Computation of kVAH: | kVA shall be computed as modulus of Active and Reactive energy. However incase of Capacitive reactive energy the kVA shall same as kW. The polarity of kVA same as kW. At No given instant the kVAH should be less than kW. | Due to design limitation at some incident KVAH would be less than KWH. We will offer meters as per previous supply. | ok
6 | Clause No. 4. Body of Meter | 1. Top transparent and base opaque material polycarbonate of Lexan 143A grade. | It is Provided with Lexan 143. It is requested to accept the same | ok
7 | Clause No. 4.3 Terminal cover: | The Terminal Cover shall be of short type and shall be transparent with polycarbonate LEXAN 143R/943A or equivalent on prior approval of the purchaser | It is Provided with Lexan 143. It is requested to accept the same. | ok
8 | Clause No. 5 Temper and Anti fraud detection evidence features | Total No. of temper events logged by the meter shall be atleast 200nos. Compartment wise division of each event and their Persistence time indicated in tamper logic list. | Compartment wise tamper events will be provided as per comments provided in clause no. 5.16. | ok
9 | Clause No. 5.2 Detection of missing Potential | The threshold of the voltage should be programmable | The threshold of the meters will be factory programmable. It is requested to accept the same | ok
10 | Clause No. 5.6 Over Load: | Meter shall Record overload as an event in terms of defined %threshold value of the load (programmable at the factory). | It should be field programmable only as per the rating of DT. However we are offering meters for net meters. Hence overload event is not required | ok
11 | Clause No. 5.10 Protection against HV Spark | Meter should be Immune to spark strength upto 35kV and above and it should record an event (occurrence and restoration) with date and time stamped. | Immunity against 35KV spark will be provided, Event logging above 35KV is not available. It is requested to accept the same. | ok
12 | Clause No. 5.16 Abnormal and Tamper Conditions | 1.) Meter shall be capable of recording occurrence and restoration of abnormal events with date and time stamped and snapshot for events such as individual voltage, current, power factor, active energy and apparent energy for export and import mode at the time of occurrence and restoration. 2.) During Abnormal condition or tamper event the current shall be recorded as active current and line current | (1.)Snap shot of only 3 energy is provided. So out of below 4 energy any 3 energy can be provided in snap shot:- 1. Active energy Import 2. Active energy Export 3. Apparent energy Import 4. Apparent energy Export It is requested to accept the same. (2.) Line current will be Provided. | ok
13 | Clause No. 5.16.1 Abnormal and Temper Conditions: | a. PT MISSING No. of event to be logged=50 B .HIGH Voltage No. of event to be logged=25 c. Voltage Unbalance No. of event to be logged=50 | Cumulative 125 Nos. voltage retaled Events (occurrence + restoration) will be provided for this compartment, it will not be separate for each event. Events will be logged on FIFO basis. Kindly accept the same. | ok
14 | Clause No. 5.16.2 Abnormal and Temper Conditions | a. CT Open No. of event to be logged=50 B .CT Bypass No. of event to be logged=50 c. Over current No. of event to be logged=25 d. Current imbalance No. of event to be logged=25 | Cumulative 150 Nos. current related events (occurrence + restoration) will be provided for this compartment, it will not separate for each event. Events will be logged on FIFO basis. Kindly accept the same. | ok
15 | Clause No. 5.16.3 Abnormal and Temper Conditions: | a. Neutral Disturbance No. of event to be logged=25 B .Magnet No. of event to be logged=25 c. Low Power Factor No. of event to be logged=25 d. HV ESD No. of event to be logged=25 | 75 Nos. event will be provided for the events related to abnormal events compartment for ND , magnet & Low Power factor. We are offeing meters as per previous supply. | ok
16 | Clause No. 5.16.1 Abnormal and Temper Conditions PT Missing: | Threshold value of restoration event: Voltage > 80% of Vref and current > 2% of Ib. | For restoration of PT missing no check of current limit is provided | As per our specification
17 | Clause No. 5.16.1 Abnormal and Temper Conditions | Voltage Unbalance: 1. Threshold value of restoration event: Shall be less than 10 between the phases and currents should be > 2% of Ib. 2. Threshold value of occurrence event: 20% or more between the phases and current > 2% of Ib | 1. Restoration limit of voltage unbalance is <20%. No check of Current limit is provided for voltage unbalance event. 2. No check of Current limit is provided for voltage unbalance event. | As per our specification
18 | Clause No. 5.16.1 Abnormal and Temper Conditions | CT Open: Threshold value of restoration event: Ir + Iy + Ib + In < 5% of Ibasic. Phase current > 10% of Ibasic with all current positive | Restoration of CT open tamper is provided when the Residual current is <10% and the Average line current >10% of Ibasic. It is requested to accept the same. | As per our specification
19 | Clause No. 5.16.1 Abnormal and Temper Conditions | CT Bypass: 1. Threshold value of restoration event: Ir + Iy + Ib + In < 5% of Ibasic. Phase current > 10% of Ibasic with all current positive. 2. Threshold value of occurrence event: Ir+Iy+Ib+In >10% of Ib and phase current>10% of Ib | 1. Restoration of CT ByPass tamper is provided when the Residual current <10% of Ib and when Average line current >10% of Ibasic. 2. Occurrence of CT Bypass event will be provided when phase current >5% of Ib. | As per our specification
20 | Clause No. 5.16.1 Abnormal and Temper Conditions | Overload Current: Threshold value of restoration event: <110% of Imax | Offered meter will log over current when <125% of Imax. It is requested to accept the same | As per our specification
21 | Clause No. 5.16.1 Abnormal and Temper Conditions | Neutral Disturbance: Persistence Time of Occurrence: 2 min. Persistence Time of Restoration: 2 min. Threshold value of restoration event: Voltage <110% of Vref, Current>2% of Ib, frequency>47Hz and frequency<52HZ. Threshold value of occurrence event: Voltage <110% of Vref, Current>2% of Ib, frequency>47Hz and frequency<52HZ, dc Voltage/signal injection. | Persistence Time of Occurrence:30 seconds Persistence Time of Restoration: 90 seconds Threshold value of restoration event: Neutral disturbance is not linked with specific frequency limit. Whenever, it gets affected on account of spurious signal injection, , Tamper with occurrence of date & time will be logged in meter as ‘Neural Disturbance’. And meter will start recording at Vref , actual current and UPF. Meter will have legend for neutral disturbance tamper on LCD display. Occurrence and restoration time will be 30 sec Approx. Threshold value of occurrence event: Neutral disturbance is not linked with specific frequency limit. Whenever, it gets affected on account of spurious signal injection, , Tamper with occurrence of date & time will be logged in meter as ‘Neural Disturbance’. And meter will start recording at Vref, actual current and UPF. Meter will have legend for neutral disturbance tamper on LCD display. Occurrence and restoration time will be 30 sec Approx. | As per our specification
22 | Clause No. 5.16.1 Abnormal and Temper Conditions | Magnet: Threshold value of restoration event: <0.5 Tesla (permanent magnet).DC Magnet induction <0.20 Tesla. AC Magnet induction <0.15 Tesla. Threshold value of occurrence event: >0.5 Tesla (permanent magnet).DC Magnet induction >0.27 Tesla. AC Magnet induction >0.2 Tesla. | Threshold value of restoration event Under influence of external magnetic field offered meter will work as per relevant IS and CBIP 304. Threshold value of occurrence event Under influence of external magnetic field offered meter will work as per relevant IS and CBIP 304. | As per our specification
23 | Clause No. 5.16.1 Abnormal and Temper Conditions | Power On-Off: Persistence Time of Restoration: 5 min | Offered meter will log immediate Power-On OFF event. It is requested to accept the same. | ok
24 | Clause No. 6.4 Display Module | Makes and Origin: Hongkong: Genda Singapore: Bonafide Technology Ever light Japan: Hitachi, Sony Korea: Advantech China: Success Holland/Korea: Phillips | Hongkong: Genda Singapore: Bonafide Technology Ever light Japan: Hitachi, Sony Korea: Advantech China: Success Holland/Korea: Phillips, Truly Semiconductor | ok
25 | Clause No. 7.1 | However the following will be printed in bar code on the meter nameplate.( Shall be printed on name plate instead on sticker) i. Manufacturer’s code No.(given by TPDDL) ii. Meter Sr. No iii. TPDDL Property iv. Month/Year of manufacture. | We can provide any 16 digit information in barcode including numbers, characters and space | As per our specification
26 | Clause No. 7.2 | 1. Bidder shall supply software suitable for energy measurement and energy spot billing through CMRI. 2. Meter Sr. No. shall be printed inside the meter top cover | 1. In the Offered Meter the Spot billing is not supported. 2. In the offered Meter the Meter Sr. No. is Printed on the rating plate. Kindly accept the same. | As per our specification
27 | Clause No. 8.2 On Demand Display: | High Resolution Cumulative Active Net Energy | Display of High resolution cumulative active net energy will not available. Kindly accept the same | As per our specification
28 | Clause No. 9.2: | Acceptance Test: Regarding Limits of error. | CONTRADICTION: Limits Specified for WC meters | ok
29 | Clause No. 9.3 | Type Test: All test are defined in IS 13779:1999 | All test are defined in IS 14697 | ok
30 | Clause No. 9.10 | Type Test Certificate: All the tests shall be conducted at the CPRI/ERDA as per relevant standard. Type Test should be conducted in Certified test Laboratory. | We have type test report form NABL accredited lab (YMPL). Type test report is available with 240V Vref. Kindly accept the same. | As per our specification
31 | Clause No. 9.15 | Tender Sample: Bidders are requiring to manufacturer 3 sample meters. | As the requirement is too low kindly revise the sample quantity of one meter for all type/ ratio of LTCT meters | ok

## WC METER
Tender No: TPNODL / OT/ 2021-22/066
Clause No. | Description |  |  |  | Manufacturer’s Reply (w.r.t. Saral 300) | TPNODL RESPONSES
1. | SCOPE : This specification covers the technical requirements of design, manufacturing, testing at meter manufacturer's works, packing, forwarding, supply and unloading at store/site of 3P 4W, 3x230 voltage, whole current NET meter of accuracy class 1.0 (here after referred as meters) complete with all accessories for efficient and trouble free operation. |  |  |  | Yes, Offered meter complies with 230V rating also but type test report are available with 240V only. | ok
2. | GENERAL TECHNICAL REQUIREMNTS
4.3 | Basic Current (Ib) & rated Maximum current (Imax): Ib= 20A; Imax= 100 Amps |  |  |  | Basic Current (Ib) & rated Maximum current (Imax): Ib= 10A; Imax= 100 Amps | Kvah Sum is required
4.23 | Self-Diagnostic feature |  |  |  | Self-Diagnostic feature will be as following.
| The meter shall have indications for un satisfactory / non-functioning of |  |  |  | 1) Self diagnostic Good | ok
| (i) Time & calendar |  |  |  |  | ok
| (ii) RTC |  |  |  | 2) Self diagnostic Oscillator Fail | ok
| (iii) RTC battery |  |  |  |  | ok
| (iv) Non Volatile Memory |  |  |  | 3) Self diagnostic RTC Fail | ok
ok
[5 empty] | 4) Self diagnostic Battery Fail | ok
ok
[5 empty] | 5) Self diagnostic Battery Low | ok
ok
[5 empty] | 6) Self diagnostic Hi temperature | ok
ok
[5 empty] | Status of RTC will be available on meter display under “self diagnostic “display parameter. Also in case of NVM & RTC failure meter will log the same as event along with date & time. | ok
[5 empty] | Status of RTC & NVM not available at BCS ends in healthy condition. | ok
4.25 | Internal diameter of the terminal holes: 9.5mm ( minimum ) Depth of the terminal holes : 25 mm. |  |  |  | Depth of terminal hole is approx. 22 mm. | ok
4.26 | Clearance between adjacent terminals : 10 mm ( minimum) |  |  |  | Center to center distance between adjacent terminals will be more than 10mm. | ok
| 4-Quadrant measurement is mandate for Net metering, meter shall be capable to measure net energy at the point of time export & import. |  |  |  | Yes, We comply with the same. However kVAh Sum (delivered + received) is not available in offered meter. | As per our specification
kWh delivered
kWh received
kWh sum
kVAh delivered (Q1+Q4)
kVAh (received) (Q2+ Q4)
kVAh Sum (delivered + received)
4.31 | Communication capabilities
4.31.1 | The meter shall have facilities for data transfer locally through CMRI PC, Laptop (through USB port) and remotely by GSM/ CDMA/ GPRS/ RF modems with proper security via an optically isolated communication port through serial communication. It shall be possible to reconfigure the meters for TOD tariff, DIP, billing date etc through proper authentication process via communication port. Optical communication port shall be available for local data downloading and RJ11 connector for remote meter data downloading. The hardware & communication ports shall not be affected by any type of injection/ unauthorized signal as per IS 13779. The complete data shall be downloaded within 2 minutes. |  |  |  | Offered meter comply as per IS: 15959. The meter will have facility to data transfer locally through windows/DOS based CMRI and laptop and remotely through GSM/GPRS Modem only. Parameters like RTC, TOD, billing date, Integration period will be reconfigure through CMRI through proper authentication. Offered meter will have additional RS232 in form of Micro USB. The complete data can be downloaded within 5 minutes. | ok
4.1.7 | The bidder shall supply software required for local “(CMRI) & remote (AMR/RMR)” including required training to use the software, free of cost. Bidder shall provide common meter reading & conversion API (as per MIOS standard) as and when required by the purchaser along with necessary support required for integration with the purchaser’s legacy system. The Api’s provided by the bidder shall work with all the meters provided by the bidder till date- i.e. the read API shall be able to download data from all the meters supplied previously also and the convert API shall convert all the data pertaining to all the meters, downloaded through CFW as well as BCS. There shall be an option of configuring reset date through CFW as well as CMRI as when required. The bidder may provide DLMS compliance additionally if possible for communication with the meter. Bidder shall be responsible to provide compatible BCS & API’s with RF communication. |  |  |  | Offered meter comply as per IS: 15959 open protocol. | ok
[5 empty] | We will supply software required for local (CMRI) & remote (AMR) connectivity including required training to use the software free of cost. | ok
| The XML files of downloaded data of the meters shall at least contain the following tags:- |  |  |  | We will provide the APIs for communication with our make of meter through local (CMRI) / remote (AMR) as and when required by TPC during warranty period. | ok
| Billing Data file – D1, D2, D3. |  |  |  | We will provide windows based common meter reading API for meter reading. | ok
| Load survey data file – D1, D2, D3, D4, D5, D6, D7, D8, D9, D10. |  |  |  | The XML files of downloaded data of the meters will be as per MIOS standards. | ok
A mandatory acceptance testing of bidder’s software shall be executed by the purchasers IT where in compatibility of Purchaser’s proprietary framework with bidder’s Read & convert API & related software would be tested and API provided should work.
4.32 | Immunity against external influencing signals |  |  |  |  | As per our specification
4.32.1 | Magnetic Field: Meter shall record accurate energy in case of any external influencing signals in line with IS 13779:1999 Cl.11.2 and variation in limits of error (upto 100% Imax) shall be as per the table 17 of IS 13779. Meter shall be immune to magnetic field such that it shall not affect the normal overall functionality However, in case of abnormal magnetic field as defined below meter shall perform as per the following actions: |  |  |  | Offered meter complies with IS 13779 & CBIP 325.
| a) Meter shall log the event in its memory as” Magnet” with date and time stamp within 2 minutes of application of abnormal magnetic field and shall start recording at 100%Imax and after removal of magnet, back to normal recording within 2 min. |  |  |  | Meter would be immune and within permissible accuracy limits as per CBIP 325 and if meter gets affected it will log magnetic event with date and time and start recording at I Max.
| b) Meter shall show TAMPER in the display. |  |  |  | Persistence time for occurrence of magnet event is 20 seconds approx. Restoration is approx. 30 seconds.
Specific Legend will be available on LCD of meter as below:-
| Abnormal Magnetic field is defined as below; |  |  |  |  | ok
| a) Continuous DC magnetic induction: >0.27 Tesla ± 5% (Value of the magneto motive force to be applied shall be generally >17500 AT, should be immune up to 0.27 T. |  |  |  | Suitable abbreviation/information will also provided under “present status other then CT & PT related events”. Display parameter. Meter would also display TAMPER icon.
b) AC magnetic induction: >10 milli Tesla ( if produced with circular metal core with square
| cross section as specified in CBIP latest report with 2800 AT)/ 0.2 T ± 5% |  |  |  | Please refer enclosed table 2 for threshold value.
c) Permanent Magnet: Immune up to 0.5T and Event logging >0.5T.
4.32.2 | Electrostatic Discharge (ESD) |  |  |  | Meter will remain immune up to 35kV and will record accurate energy as per IS-13779. Meter does not have provision for logging of any event above 35kV spark. Accuracy & functionality of meter is not guaranteed during spark. | As per our specification
| Meter shall be immune up to 50 kV ESD and shall record accurate energy – Mater shall log (occurrence & restoration) of event into memory as “HV ESD” with date & time stamp and instantaneous parameters (Voltage, Phase current, Neutral current, Power factor, Frequency, Energy active & apparent for both export & import mode for any ESD greater than 50 kV and shall show TAMPER on Display. |  |  |  | Meter does not have provision to record instantaneous parameters (Voltage, Phase current, Neutral current, Power factor, Frequency, Energy active & apparent for both export & import mode and also TAMPER indication on display is not available, event will be logged as abnormal external interference and can be viewed at BCS.
4.33.0 | DC / AC injection |  |  |  |  | As per our specification
| The meter shall not saturate on passage of direct current, which can cause the meter either to stop recording/ record inaccurately. DC injection shall be tested both in phase and neutral. Measurement by meter shall not get influenced by injection of Chopped signal/ DC signal/ DC pulse upto 330V and for any value beyond this. Meter shall log the event into memory as ‘Neutral Disturbance’ with date & time stamp and shall show ‘TAMPER’ in the display after time delay of 2 min (occurrence & restoration). |  |  |  | Meter will remains either immune or if it gets affected meter will log ND event & record energy at V-ref X Actual current X UPF. Accuracy will be ±4%. Specific Legend can be provided on LCD of meter
| The meter shall record energy proportional to current & V ref (230V) when any of the tamper circuits used to tamper energy using a diode or a variable resistance or a variable capacitor energy saving devices. The measurement by meter shall not get influenced by injection of AC voltage / Chopped signal/ DC signal / DC pulse of low frequency and harmonics. In case the meter accuracy is disturbed under Neutral disturbance it should be able to log event. |  |  |  | Persistence time for Occurrence would be 20-30seconds and for restoration would be approx. 90 sec.
Neutral disturbance logic will be as per our standard logic
Please refer table 2 for threshold value.
4.34 | Abnormal Tamper conditions |  |  |  |  | ok
4.34.1 | The meter shall be capable of recording occurrence & restoration of abnormal events listed below along with date & time and snap shots of individual voltages, currents, power factors, active energy and apparent energy for export & import mode at the time of occurrence of abnormal event and restoration of normal supply. During abnormal & Tamper conditions, the current shall be recorded as active current & line current. Each such event shall be provided compartment wise as mentioned below due to limitation of FIFO. |  |  |  | Events will log as per prevailing electrical conditions.
Offered meter have event logging as per IS: 15959. However in case meter record tamper, it will log snap shot on confirmation of event i.e. after persistence time of occurrence or restoration. Considering restoration & occurrence events as separate event. Snap shot will be Voltage , Line current, Neutral current, power factor & configured energy.
4.34.2 | Comp. No. | Description | Event Logged | Snapshot parameters: Phase voltages, currents (both phase & neutral), power factor phase wise, Frequency, active energy and apparent energy for export & import mode | Offered meter have event logging as per IS 15959. Events within a compartment will be logged in FIFO basis and no. of events assigned will be compartment wise not with individual tamper.
| 1 | PT Missing | 50 | Yes | i. Voltage related event (Over voltage, low voltage, voltage missing, voltage unbalance) -150 Nos.
|  | Voltage Unbalance | 50 |  | ii. Current related events (CT open CT by pass, Current reversal, current imbalance & over current – 200 Nos.
|  | High Voltage | 25 |  | iii. Other Events (Magnet, ND, Low power factor) -150 Nos.
| 2 | CT open | 50 | Yes | iv. Non roll over – Cover open (5 nos.)
|  | CT Bypass | 50 |  | v. Power failure – 100 Nos.
|  | Over current | 25 |  | However, in case meter record tamper, it will log snap shot on confirmation of event i.e. either occurrence or restoration. Snap shot on confirmation of event i.e. either occurrence or restoration
|  | Current Imbalance | 25
| 3 | Neutral Disturbance | 25 | Yes | There is a contradiction in Both the clause 4.34.1 & 4.34.2. Frequency is not available in event snapshots.
|  | Magnet | 25
|  | Low Power Factor | 25
|  | HV ESD | 25
| 4 | Power on off | 25 | No
| 5 | Cover Open | 5 | Yes
4.34.3 | Meter shall be immune to influence of magnet and HV ESD in all conditions as defined above. If value of magnet/ ESD is abnormal then Tamper event shall be logged. |  |  |  | Meter would be immune and within permissible accuracy limits as per CBIP 325 and if meter gets affected it will log magnetic event with date and time and start recording at I Max. | ok
Specific Legend will be available on LCD of meter as below:-
Meter will remain immune up to 35kV and will record accurate energy as per IS-13779. Meter does not have provision for logging of any event above 35kV spark. Accuracy & functionality of meter is not guaranteed during spark.
4.34.4 | All the tamper events i.e. MAGNET/ HV ESD/ Meter Top cover open/ ND/ shall be logged in memory of the meter with date & time stamp. Cumulative tamper count shall be increased by 1 and tramper events shall be displayed in push button mode. |  |  |  | All the tampers i.e. MAGNET / Meter Top cover open/ ND/ would be logged in memory of the meter with date & time stamp. | As per our specification
Meter will remain immune up to 35kV and will record accurate energy as per IS-13779. Meter does not have provision for logging of any event above 35kV spark.
For Tamper Events suitable abbreviations would be available on display under
Present Status of PT related tampers.
Present Status of CT related tampers.
Present status of Other tampers.
| Components should be upgraded as per latest available design/ make. |  |  |  | Please refer enclosed component make sheet
5.1 | Meter Body |  |  |  |  | ok
| Meter body shall be made of unbreakable, high grade, fire retardant reinforced Insulating material (protective Class II) with FV0 Fire Retardant, self - extinguishing, UV stabilize, recyclable and Anti oxidation properties. |  |  |  | The meter case and ETBC will be FV2 Compliant & Meter terminal block will be FV0 compliant.
However material will be:
| The minimum thickness of the meter enclosure shall be 2mm. |  |  |  | Meter case: LEXAN 143A/943 Equivalent
Terminal Block: LEXAN 500/equivalent
Material of meter will meets the requirement of IS 13779
Thickness will be 2mm ± 0.2mm.
| Meter base shall be opaque with virgin polycarbonate LEXAN 500R or equivalent on prior approval from purchaser . |  |  |  | Offered meter have opaque single enclosure design i.e. integrated base & cover. Having transparent window for display LCD.
Meter case: LEXAN 143A/943 Equivalent
Material of meter will meets the requirement of IS 13779
| Unidirectional screws to be used on meter covers where ever required. |  |  |  | Not applicable for our design, Offered meter have single enclosure design i.e. integrated base & cover design. Thus nullifying the possibility of opening of meter case.
5.2 | Terminals, Terminal Block |  |  |  |  | As per our specification
| Terminal block should be single mould with meter body base. (Not seperate) |  |  |  | Not applicable for our design, Offered meter have single enclosure design i.e. integrated base & cover design. Meter cover is attached to terminal block with chemical welding.
| Terminal block and terminal cover shall be of a material which complies with the requirements of IS11731 (part 1) method FH1. The material of which the terminal block is made shall be capable of passing the test given in ISO 75 for temperature of 135°C and pressure of 1.8 M Pa. |  |  |  | Heat Deflection temperature test will be for a temperature of 120°C ± 5°C.
| The manner of fixing the conductors to the terminals shall ensure adequate and durable contact such that there is no risk of loosening or undue heating. Terminals shall be bottle type not cage clamp shall be preferably of MS cage clamp type as per IS: 15707 or of flat end screw with atleast 9 mm dia of screw for better contact area. |  |  |  | At incoming/Supply side High tension spring is used for Clamping the external leads or thimbles, hence re-termination can’t be done. & In load side, cheese head screw of Zn plated MS is provided.
One the connection is made at supply side with locking arrangement, then it is not possible to open the connection (to overcome the chances of tampering). Even if supply side wire is cut then it is not possible to connect the same.
The terminals inserts and screws will be made of Zn plated MS.
In supply side, permanent locking arrangement of supply cable is provided, hence plastic type screws will be provided for such arrangement. The function of these screws are only to release the locking arrangement, it will not carry current.
In load side, cheese head screw of Zn plated MS is provided
| Internal diameter of the terminal holes shall be minimum 9.5 mm; minimum clearance between adjacent terminals shall be 10 mm. Minimum Depth of the terminal holes shall be of 25mm. |  |  |  | Yes, We comply with the same
Clearance between adjacent terminals will be 15 mm approx. (centre to centre).
Depth of terminal hole will be approx.. 22 mm.
5.3 | Terminal Cover |  |  |  |  | ok
| Terminal cover shall be of short type and shall be transparent with polycarbonate LEXAN 143R/943A or equivalent on prior approval from the purchaser. |  |  |  | Terminal cover will be transparent extended type with polycarbonate LEXAN 143A/943 or equivalent material.
| Appropriate space shall be available for incoming /outgoing cables without damaging/ stressing terminal cover (terminal cover design shall be as per the purchaser approval). After sealing the cover, terminals shall not be accessible without breaking the seals. |  |  |  | Yes. Complied.
One U cut of 60 x 40 mm will be provided in ETBC available for incoming/outgoing cable
5.4 | Sealing of meter |  |  |  | Meter case will have screw less design (single enclosure), hence same is not applicable. However on no. sealing hole will be provided between meter case (base & cover) and terminal block for placing either utility seal or bidders seal. | ok
| Reliable sealing arrangement shall be provided to make the meter tamper evident and to avoid fiddling or tampering by unauthorized persons. |  |  |  | Provision for one hologram seal will be available.
For this, one no. Polycarbonate seal and 1 no. Hologram seal shall be provided by the Purchaser.
| One no. Polycarbonate seal and 2 no. Hologram seal shall be provided by the Bidder. |  |  |  | For utility sealing purpose two no. sealing screw will be provided on ETBC.
All the seals shall be fixed on meter body by the bidder at his works before dispatch.
Two sealing provision shall be provided at meter terminal cover, such that terminal shall not be accessible without breaking the seals. Length of the seal wire should not be loose, that meter top cover should not be opened without breaking/ cutting the seal wire. All the seals shall be provided on front side only and as per the TPADL specification. Rear side sealing arrangement shall not be accepted. Bidder shall provide seals be as per CEA regulation (2006). Only patented seals to be used as per CEA requirements.
The bidder shall be open to further modifications in the software if required by the purchaser free of cost.
a) Remote configuration through AMR should be possible
b) Software data files and system files should be stored in different directories.
c) Real time clock should be based on Quartz crystal timer so as to make it independent of line frequency. Manual & remote synchronization with server shall be made possible.
d) The meter should have hardware/ software locking for programming change of parameters & the same should be protected with 2 level password.
e) Record number files should be 12 digits alphanumeric for unique contact account no. (CA no.)
5.6 | MD Integration |  |  |  | Yes comply with the same, | ok
| The MD integration period shall be 30 minutes (integration period-programmable by CMRI at site and also through AMR with adequate security level). The MD resetting shall be automatic at the 1st of the month i.e. 0000 hours of 1st day of the month. Last six MD values shall be stored in the memory and 4 to be displayed in the auto scroll mode. MD shall be recorded and displayed with minimum three digits before decimal and minimum two digits after decimal points. MD integration shall be of sliding Type not in time block . |  |  |  | However only 3 month history of MD can be provided on meter display in Auto mode. At the BCS end 12 month history of MD is available.
5.7 | Load survey |  |  |  |  | ok
| The meter shall be capable of recording 30 minutes average of the following parameters for at least last 90 days |  |  |  | We comply with the same.
| 1. Voltage per phase |  |  |  | However,
| 2. Current per phase |  |  |  | In the offered meter, the following parameters are not provided:
| 3. Power Factor per phase |  |  |  | Power factor phase wise.
| 4. Average kWh import |  |  |  | Average kWh net, Average kVAh net, Average kVArh lagging net and Average kVArh leading Net.
| 5. Average KVAH import |  |  |  | It is requested to accept the same.
6. KVArh lagging import
| 7. KVArh leading import |  |  |  | Load survey parameters will be as below.
| 8. Average kWh export |  |  |  | 1. Voltage per phase
| 9. Average KVAH export |  |  |  | 2. Current per phase
| 10. KVArh lagging export |  |  |  | 3. Cal. Avg. power factor.
| 11. KVArh leading export |  |  |  | 4. Average kWh import
| 12. Average KWh Net |  |  |  | 5. Average KVAH import
| 13. Average KVAH Net |  |  |  | 6. Average kWh export
| 14. KVArh lagging Net |  |  |  | 7. Average KVAH export
| 15. KVArh leading Net |  |  |  | 8. Reactive import while Active import (Q1)
| 16. Demand KW import |  |  |  | 9. Reactive import while Active export (Q2)
| 17. Demand KVA import |  |  |  | 10. Reactive export while Active export (Q3)
| 18. Demand KVArh lag import |  |  |  | 11. Reactive export while Active import (Q4)
| 19. Demand KVArh lead import |  |  |  | 12. Demand KW import
13. Demand KVA import
14. Demand KVArh lag import
15. Demand KVArh lead import
5.8 | Display units |  |  |  | Yes, complied. However LCD display will have a wide viewing angle of 60 Deg & The kWh & KVAh register will have 7 digits with display digit size 8.5 X 3.4 mm. Suitable to view parameters from distant. | ok
| The display unit shall be Pin type built-in liquid crystal display (Permanently backlit type LCD green color). The LCD shall be of STN (Super Twisted Nematic) construction suitable for maximum temperature withstands 65˚C and minimum temperature withstands 0 ˚C during normal operating condition. The LCD display shall have a wide viewing angle of 120 degree. When the meter is not energized the electronic display need not be visible. The display shall not be affected by electrical, magnetic disturbances and ESD. |  |  |  | High regulation energy in Wh & VAh with 6+1 digits is provided.
The back lit must be green in color while in normal registration modes.
The kWh register shall have minimum 7 digits and size of the digits shall be minimum 10mmx5mm. Cumulative energy (kWh) shall be displayed without decimal in auto scroll mode. (However decimal shall be available in push button mode for high resolution display for testing).
| Auto Scroll mode |  |  |  | Following display parameter are not available | As per our specification
Following parameters shall be displayed in Auto Scroll mode in the given order.
5.8.2 | Push button mode |  |  |  | Following display parameter are not available | As per our specification
5.9 | 5.9.1 Pulse Rate: The meters shall have a suitable test output device. Red color blinking LED (marked as imp/kWh) shall be provided in the front left side. One more Red color blinking LED shall be provided in the front right side and shall be configurable through push button. This device shall be suitable for using with sensing probe used with test benches or reference standard meters. The test output device shall have impulse rate defined as impulse / kWh & pulse/kVArh. imp / unit should be 800 for each type energy unit kWh/ kVArh. |  |  |  | Yes, We comply with the same.
However, Pulse rate of meter will be 1600 Pulse/unit & it will be printed on rating plate
6 | NAME PLATE AND MARKING |  |  |  | Offered meter have single enclosure design. Rating plate information will be laser printed on meter base. | ok
Meters name plate parameters should be laser printed and inside the top cover. Meter shall have a name plate clearly visible and effectively secured against removal. Indelibly and distinctly marked with all essential particulars as per relevant standards along with the following.
The meter will have manufacturer specific 10 alpha-numeric digit serial no. & Barcode will contain manufacturer specified meter Sr. Nos. only (laser printed). All other information will be laser printed on rating plate.
| i. Manufacturer's name |  |  |  | Two bar codes will be provided one for Sr. No. and Other one Bar code will contain detail of TPDDL, Month & year of manufacturing.
ii. Type designation
iii. Number of phases and wires
iv. Serial number.
v. Month and Year of manufacture
vi. Unit of measurement
vii. Reference voltage ,
viii. frequency
ix. Ref. temperature if different from 27 deg. C
x. Rated basic and maximum Current
xi. Meter constant (imp/kWh)
xii. ‘BIS’ Mark
xiii. Class index of meter
xiv. "Property of TPDDL”
xv. Purchase Order No. & date
xvi. Guarantee period.
xvii. Rated frequency
xviii. Sign of double square
xix. Country of manufacture.
However the following shall be printed in bar code on the meter nameplate.
Manufacturer’s code No. (Given by TPDDL)
Meter Sr. no.
TPDDL property.
Month/ year of manufacturing.
7.2 | ACCEPTANCE TEST |  |  |  | Acceptance test will be performed as per IS 13379. | ok
1) AC High Voltage test
2) Insulation test
3) Test on limits of error with following loads:
4) Test of meter constant
5) Test of starting current
6) Test of no load condition
7) Test of repeatability of error
8) Test of power consumption
7.3 | TYPE TEST |  |  |  | Yes, we comply. | ok
| 1) All tests as defined in IS 13779:1999, |  |  |  | However DC immunity test would be as per IS 13779.
2) Test against abnormal magnetic influence as per CBIP TR 88.
3) DC immunity test (injection both on phase & neutral terminals)
4) Test for material used for terminal block and meter body as per relevant standards.
8 | TYPE TEST CERTIFICATE |  |  |  | Enclosed along with bid for ready reference. We have type test report form YMPL lab | As per our specification
The bidder shall furnish the type test certificates of the meter for the tests as mentioned above as per the corresponding standards. All the tests shall be conducted at CPRI/ ERDA as per relevant standards.
Type test should have been conducted in certified Test Laboratories during the period not exceeding 5 years from the date of opening the bid. In the event of any discrepancy in the test reports i.e. any test report not acceptable or any/all type tests (including additional type tests, if any) not carried out, same shall be carried out without any cost implication to NDPL .
9 | PRE-DESPATCH INSPECTION |  |  |  | Noted | As per our specification
| Inspection can be conducted at any stage of manufacture at the discretion of the TPADL and the equipment, if found unsatisfactory as to workmanship or material, the same is liable to rejection. |  |  |  | Leaflet will be provided in soft copy only
Equipment shall be subject to inspection by a duly authorized representative of the TPADL.
Bidder shall grant free access to the places of manufacture to TPDDL's representatives
at all times when the work is in progress. Inspection by the TPDDL or its authorized representatives shall not relieve the bidder of his obligation of furnishing equipment in accordance with the specifications. Material shall be dispatched after specific MDCC (Material Dispatch Clearance Certificate) is issued by TPDDL .
Following documents shall be sent along with material:
a) Pre dispatch Inspection Test reports
b)MDCC issued by TPADL
c)Invoice in duplicate
d)Packing list
e)Drawings & catalogue
f) Guarantee / Warrantee card
g)Delivery Challan
h)Other Documents (as applicable)
10 | INSPECTION AFTER RECEIPT AT STORE |  |  |  | Yes, We comply with the same. | As per our specification
The material received at purchaser's store shall be inspected for acceptance and shall be liable for rejection, if found different from the reports of the pre-dispatch inspection and one copy of the report shall be sent to Project engineering department.
Please clarify the requirement of 2 extra boxes, we understand that 2 nos. extra empty boxes are required.
The successful bidder shall submit 2 extra boxes (unpaid) per lot delivereds, with serial no. in continuation to the lot (lot size shall be 2000 nos. or as defined in order) to purchaser for further testing & confirmation in line with the specifications and the m,aterial shall be liable for rejection, if test results are found different from the reports of the pre dispatch inspection and one copy of the report shall be sent to project engineering department.
11 | GUARANTEE |  |  |  |  | As per our specification
| Bidder shall stand guarantee towards design, materials, workmanship & quality of process / manufacturing of items under this contract for due and intended performance of the same, as an integrated product delivered under this contract. In the event any defect is found by the purchaser up to a period of at least 60 months from the date of commissioning or 66 months from the date of last supplies made under the contract whichever is earlier, Bidder shall be liable to undertake to replace/rectify such defects at its own costs, within mutually agreed time frame, and to the entire satisfaction of the Company, failing which the purchaser will be at liberty to get it replaced/rectified at bidder’s risks and costs and recover all such expenses plus the Company’s own charges (@ 20% of expenses incurred), from the bidder or from the “ Security cum Performance Deposit” as the case may be. |  |  |  | The offered Meters will be guaranteed for a period of 60 months from the date of commissioning or 66 months from the date of last supply whichever is earlier. We also agree to repair / replace defective meters within one month period, from the date receipt of defective meters.
Any defect in the material/equipment/components found during Guarantee period will be replaced/repaired by us provided the defect is due to bad quality of raw material, bad workmanship or faulty design.
Bidder shall further be responsible for for free replacement at site for another period of 3 years from the end of guarantee period for any latent defects if noticed and reported by purchaser.
12 | PACKING |  |  |  |  | As per our specification
| 1. Bidder shall ensure that all material covered under this specification shall be prepared for rail/road transport (local equipment) and be packed in such a manner as to protect it from damage in transit. The material used for packing shall be environmentally friendly. Packing and transportation shall be as per IS 15707:206 clauses 9.1 and 9.2. Routine test report of the individual meter shall be kept inside each card board carton of the meter. |  |  |  | Noted 12 nos. meters will be packed in one corrugated box, not individual meter.
13 | SAMPLE |  |  |  | Noted | As per our specification
| Tendering stage: |  |  |  | However for such small quantity (100 nos.) providing 3 nos. samples is not feasible, so 1 no 3P WC Net meter sample can provided.
Bidders are required to manufacture 03 numbers of sample meters as per the NDPL specification (sealed, unsealed and openable base and cover to view/test the inner circuits) and submit the samples (non-returnable) along with bid for approval.
14 | QUALITY CONTROL |  |  |  | Yes, We comply with the same. | ok
The bidder shall submit with the offer Quality assurance plan indicating the various stages of inspection, the tests and checks which will be carried out on the material of construction, components during manufacture and bought out items and fully assembled component and equipment after finishing. As part of the plan, a schedule for stage and final inspection within the parameters of the delivery schedule shall be furnished.
15 | Quality should be ensured at the following stages:
| 1. At PCB manufacturing stage, each board shall be subjected to computerized bare board testing. |  |  |  | 1. Noted.
| 2. At insertion stage, all components should undergo computerized testing for conforming to design parameter and orientation. |  |  |  | 2. Noted
| 3. Complete assembled and soldered PCB should undergo functional testing using Automatic Test Equipment (ATEs). |  |  |  | 3. Noted
| 4. Prior to final testing and calibration, sample meters shall be subjected to aging test (i.e. meters will be kept in ovens for 24 hours at 55 Deg. C temperature and atmospheric humidity under real-life condition at its full load current. After 24 hours meter should work satisfactorily. |  |  |  | 4. This test is not performs at our works
Component
S.No. | Component make | Makes & origin
1 | Clause No. 5.0.1 Measuring/Computing Chips | USA: Analog Devices, Cyrus, Logic, Atmel, Phillip.
| Makes and origin: USA: Analog Devices, Cyrus, Logic, Atmel, Phillip. | South Africa : SAMES
| South Africa : SAMES | Japan: NEC, 1. Free scale semiconductor
| Japan: NEC | NXP or any other reputed make shall also be acceptable
2 | Clause No. 5.0.2 Memory Chips: | USA: Atmel, National Semiconductor, Texas Instruments, Phillips.
| Makes and Origin: USA: Atmel, National Semiconductor, Texas Instruments, Phillips. | Japan: Hitachi ,Oki, 2. ST, Microchip
| Japan: Hitachi ,Oki | Macronix , ROHM or any other reputed make shall also be acceptable
3 | Clause No. 5.0.3 Display Module | Taiwan: Holtek
| Makes and origin: Taiwan: Holtek | Singapore: Modified Technologies
| Singapore: Modified Technologies | Korea: Advantek
| Korea: Advantek | China: Xiamen
| China: Xiamen | Truly semiconductor
Integrated with microcontroller, Tianma or any other reputed make shall also be acceptable
4 | Clause No. 5.0.4 Optical Port | USA: National Semiconductor
| Makes and Origin: USA: National Semiconductor | Holland/Korea: Phillips
| Holland/Korea: Phillips | Taiwan: Maxim
| Taiwan: Maxim | Japan : Hitachi, Everlight
| Japan : Hitachi | Everlite or any other reputed make shall also be acceptable
5 | Clause No. 5.0.5 Electronic Computer: | USA: National Semiconductor, Phillips, Texas Instruments.
| Makes and origin: USA: National Semiconductor, Phillips, Texas Instruments. | Japan: Hitachi, OKI, AVX or Ricoh.
| Japan: Hitachi, OKI, AVX or Ricoh. | Korea: Samsung
| Korea: Samsung | Vishay or any other reputed make shall also be acceptable
6 | Clause No. 5.0.7 Battery | Varta/Tandirun/Sanyo or equivalent/ Vitzrocell,
| Makes and origin: | EVE, Xeno or any other reputed make shall also be acceptable
Varta/Tandirun/Sanyo or equivalent.
7 | Clause No. 5.0.8 RTC/Micro controller | Built into microcontroller, USA: Phillips, Dallas, Atmel, Motorola
| Makes and origin: USA: Phillips, Dallas, Atmel, Motorola | Japan: NEC,OKI,
| Japan: NEC,OKI | Mitsubishi or any other reputed make shall also be acceptable

## HT CONSUMER
Tender No: TPNODL / OT/ 2021-22/066
S. no | Persistence time for occurrences | Persistence time for Restoration | Threshold value for Occurrence of events | Threshold value for restoration of events | Compartment size | TPNODL RESPONSES
1 | ESD/ Jammer= Immediate( record only 1 event on first application & only one events for next 1 min | ESD/Jammer =0 Hr 01 min 0 sec (ESD)( should restore after 1 min of last application) | Immunity up to 50KV | Removal of ESD/ jammer signal | 25 | ok
2 | Magnet = 0Hr 2min 0 sec (MAG) | Magnet=0 Hr 2 Min 0 sec (MAG) | >0.5 tesla for permanent magnet or DC magnetic induction > 0.2T Or AC magnetic induction>10mT | <0.5 tesla for permanent magnet or DC magnetic induction <0.2T Or AC magnetic induction<10mT | 25 | ok
3 | Meter top cover open(TC open) immediate | Meter top cover open(TC open) immediate | If meter top cover is opened | NA | 05( stay put type) | ok
4 | Potential Missing = 0 Hr 10 Min 0 sec (PM) | Potential Missing = 0 Hr 2 Min 0 sec | Voltage < 70% of Vref AND current > 2% Ibasic | Voltage > 80% of Vref AND current > 2% Ibasic | 25 | ok
5 | Voltage Unbalance = 0 Hr 30 Min 0 sec (VU) | Voltage Unbalance = 0 Hr 2 Min 0 sec | 20% or more between the phases and current > 2% Ibasic | Shall be less than 10 % between the phases and current > 2% Ibasic | 25 | ok
6 | CT Open (phase wise) = 0 Hr 10 Min 0 sec | CT Open (phase wise) = 0 Hr 2 Min 0 sec | Ir + Iy + Ib + In ≥ 10 % of Ibasic (vector Sum ) AND Phase current < 1% of Ibasic with All current positive | Ir + Iy + Ib + In < 5 % of Ibasic. (vector Sum) AND Phase current > 10% of Ibasic with All current positive | 25 | ok
7 | Invalid Phase assoication | Invalid Phase association (Immediate) | Incorrect Phase association | Correct phase connections | 25 | ok
8 | CT Reversal = 0 Hr 30 Min 0 sec (CTR) | CT Reversal = 0 Hr 2 Min 0 sec | Active current Negative 0 .2 % of Ib | Active current positive AND > 2 % Ibasic | 25 | ok
9 | CT Bypass = 0 Hr 10 Min 0 sec (CTB) | CT Bypass = 0 Hr 2 Min 0 sec | Ir + Iy + Ib + In ≥ 5 % of Ibasic (vector Sum) AND any Phase current > 10% of Ibasic with All current positive | Ir + Iy + Ib + In < 2.5 % of Ibasic. (vector Sum) AND any Phase current > 10% of Ibasic with All current positive | 25 | ok
10 | Current Unbalance = 0 Hr 30 Min 0 sec (CU) | Current Unbalance = 0 Hr 2 Min 0 sec | Current difference > 20% between phases and I min 10% of Ibasic | Current difference < 10% between the phases and I min>10% of Ib | 25 | ok
11 | Low Power Factor = 0 Hr 30 Min 0 sec (LPF) Low | Power Factor = 0 Hr 2 Min 0 sec | Phase wise Power Factor ≤ 0.5 in any phase | Phase wise Power Factor ≤ 0.7 in respective phase | 25 | ok
12 | Neutral disturbance 0 hr 1 min 0 sec(ND) | Neutral disturbance 0 hr 2 min 0 sec(ND) | Voltage >145% of vref Current >10% of Ib or frequency 47 Hz or frequency >53 Hz or DC voltage/ signal injection/ as per the condition of clause 4.3.4 | Voltage <115% of Vref current>10% of Ib & frequency >47 or freq<52 Hz | 25 | ok
13 | Power off = 0Hr 05 min 0 sec | Power on = immediate | Actual voltage off | Actual power on | 25 | ok
14 | Over Voltage = 0 Hr 30 Min 0 sec | Over Voltage = 0 Hr 2 Min 0 | Voltage > 130% of Vref | Voltage <110% of Vref | 25 | ok
15 | Over current (if enabled) OL 0 Hr 30 min 0 sec | Overload (if enabled) OL 0 Hr 2 min 0 sec | Present value (default set at 120% Ib) | <100% Ib | 25 | ok
16 | Microwave immediate(record only 1 event on first application & only one event for next 1 min) | Microwave 0 hr 01min 0 sec (should restore after 1 min of last application) | Any higher frequency magnetic waves, micro waves>10mT | Removal of device | 25 | ok

## TEMPER LOGIC COMPONENT FOR WC
Tender No: TPNODL / OT/ 2021-22/066
Tamper Logic threshold for 3Phase WC Meter
Compartment | Tamper Event | Size | Occurrence | Time of Occurrence | Restoration | Time of Restoration | TPNODL RESPONSES
Voltage related | Potential Missing | 150 | Voltage < 60% of Vref AND current > 2% Ibasic | 5 min | Voltage > 70% of Vref AND current - Ignore | 5 min | ok
| High Voltage |  | Voltage > 115% of Vref | 5 min | Voltage < 110% of Vref | 5 min | ok
| Voltage Unbalance |  | Vmax-Vmin> 20% Vmax Line current- ignore | 5 min | Vmax-Vmin < 20% Vmax Line current- ignore | 5 min | ok
Current related | CT Open | 200 | Residual Current >10% Ib Ix< 1% Ib | 5 min | Residual Current< 10% Ib Average Current >10% of Ib | 5 min | ok
| CT Bypass |  | Residual Current >10% Ib Ix>10% Ib | 5 min | Residual Current >10% Ib Average Current >10% of Ib | 5 min | ok
| Over current |  | Ix> 100 % Imax | 5 min | Ix< 100 % Imax | 5 min | ok
| Current Unbalance |  | Vmax - Vx < 20% Vmax, Ix > 10% Ib Imax - Ix >= 30% Ib | 15 min | Vmax - Vx < 20% Vmax Ix > 10% Ib Imax - Ix =< 20% Ib | 15 min | ok
Power failure | Power on/off | 100 | Actual voltage off | 5 min | Power resume | Immediate | ok
Other event | Neutral disturbance | 150 | In case meter is get affected by external signal injection (chopped DC, Chopped AC & Dc injection through diode) or both active | 20 sec-30 sec | If neutral is restored and meter is in normal condition | 90 Sec | ok
| Magnet |  | Whenever meter sense abnormal magnetic field it shall record active and apparent energy at I max at UPF | 30sec | If magnet is removed and meter is in normal condition | 30sec | ok
| Low Power Factor (Not phase wise) |  | Power Factor ≤ 0.5 Line Current >10% of Ibasic | 5 min | Power Factor > 0.5 Line Current >01% of Ibasic | 5 min | ok
Non roll over event | Meter Top Cover Open (TC Open) | 5 | If meter top | immediate | NA | NA | As per our Specification
cover is
opened
S.No. | Component make | Makes & origin | TPNODL RESPONSES
1 | Clause No. 5.0.1 Measuring/Computing Chips | USA: Analog Devices, Cyrus, Logic, Atmel, Phillip. | ok
| Makes and origin: USA: Analog Devices, Cyrus, Logic, Atmel, Phillip. | South Africa : SAMES
| South Africa : SAMES | Japan: NEC, 1. Free scale semiconductor
| Japan: NEC | NXP or any other reputed make shall also be acceptable
2 | Clause No. 5.0.2 Memory Chips: | USA: Atmel, National Semiconductor, Texas Instruments, Phillips.
| Makes and Origin: USA: Atmel, National Semiconductor, Texas Instruments, Phillips. | Japan: Hitachi ,Oki, 2. ST, Microchip
| Japan: Hitachi ,Oki | Macronix , ROHM or any other reputed make shall also be acceptable | ok
3 | Clause No. 5.0.3 Display Module | Taiwan: Holtek
| Makes and origin: Taiwan: Holtek | Singapore: Modified Technologies
| Singapore: Modified Technologies | Korea: Advantek
| Korea: Advantek | China: Xiamen
| China: Xiamen | Truly semiconductor
|  | Integrated with microcontroller, Tianma or any other reputed make shall also be acceptable | ok
4 | Clause No. 5.0.4 Optical Port | USA: National Semiconductor
| Makes and Origin: USA: National Semiconductor | Holland/Korea: Phillips
| Holland/Korea: Phillips | Taiwan: Maxim
| Taiwan: Maxim | Japan : Hitachi, Everlight
| Japan : Hitachi | Everlite or any other reputed make shall also be acceptable | ok
5 | Clause No. 5.0.5 Electronic Computer: | USA: National Semiconductor, Phillips, Texas Instruments.
| Makes and origin: USA: National Semiconductor, Phillips, Texas Instruments. | Japan: Hitachi, OKI, AVX or Ricoh.
| Japan: Hitachi, OKI, AVX or Ricoh. | Korea: Samsung
| Korea: Samsung | Vishay or any other reputed make shall also be acceptable
6 | Clause No. 5.0.7 Battery | Varta/Tandirun/Sanyo or equivalent/ Vitzrocell,
| Makes and origin: | EVE, Xeno or any other reputed make shall also be acceptable | ok
Varta/Tandirun/Sanyo or equivalent.
7 | Clause No. 5.0.8 RTC/Micro controller | Built into microcontroller, USA: Phillips, Dallas, Atmel, Motorola
| Makes and origin: USA: Phillips, Dallas, Atmel, Motorola | Japan: NEC,OKI,
| Japan: NEC,OKI | Mitsubishi or any other reputed make shall also be acceptable | ok

## COMMERCIAL QUERY
Tender No: TPNODL / OT/ 2021-22/066
Sr. No. | Detailed Reference to Tata Power Tender Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | TPNODL RESPONSE
1 | 2 | 3 | 4
1 | Sl. No. 1.3 Calendar of Events Page No. 3 | (f) Last date and time of receipt of Bids 01.010.2021 up to 1500 Hours | we request you to kindly extend tender submission due date to at least 4 to 6 weeks from the date of issued of clarifications / amendments. | Not Acceptable
2 | Clause no. 13 SAMPLE Page No 96 | Tendering stage: Bidders are required to manufacture 03 numbers of sample meters as per the TATA POWER-DDL specification (sealed, unsealed and open able base and cover to view/test the inner circuits) and submit the samples (non-returnable) along with bid for approval. These samples should be submitted at Meter Testing Lab, Rohini Sector 13. | It is not possible to submit Tender Samples at such short period and since we are regular supplier of Tata power In-view of the above we request you to kindly waive-off Tender Sample submission | As per Tender specification
3 | Clause No. 13.0 TENDER SAMPLE Page No. 42 | Tendering stage: Bidders are required to manufacture 03 numbers of sample meters as per the TPNODL specification (sealed, unsealed and open able base and cover to view/test the inner circuits) and submit the samples (non-returnable) along with bid for approval. These samples should be submitted at TPNODL store. |  | As per Tender specification
4 | Clause No. 13.0 TENDER SAMPLE | Bidders are required to manufacture 03 sample meters as per the TPC specification (sealed, unsealed and openable base and cover to view/test the inner circuits) and submit the sample (non-returnable) along with bid |  | As per Tender specification
| Clause No. 13.0 TENDER SAMPLE | Bidders are required to manufacture 03 sample meters as per the TPC specification (sealed, unsealed and openable base and cover to view/test the inner circuits) and submit the sample (non-returnable) along with bid |  | As per Tender specification
5 | GENERAL CONDITIONS OF CONTRACT FOR SUPPLY ORDERS Clause No. 13.6 Latent Defect Page No. 15 of 45 | Hidden defects in manufacturing or design of the product supplied and which could not be identified by the tests conducted but later manifested during operation of the equipment are termed as latent defects. Associates shall further be responsible for ‘free replacement’ for another period of THREE years from the end of the guarantee period for any ‘Latent Defects’ if noticed and reported by the Company. | Energy Meters shall be Guaranteed for 60 Months from the date of Suppy. 5 Years time period is sufficient for Latent Defect if any. So, we request you to kindly remove this clause. | As per Tender specification
6 | GENERAL CONDITIONS OF CONTRACT FOR SUPPLY ORDERS Clause No. 14 (a) LIQUIDATED DAMAGES Page No. 16 of 45 | For delay of each week and part thereof from the delivery schedule specified in thecontract, 1% of contract value corresponding to undelivered quantity, provided full quantity is supplied within 130% of the original contract time. If full contractual quantity is not delivered within 130% of contract time for delivery, TPC has the right to levy LD on the entire contract value, subject to a maximum of 10% of the total contract value. | we request you to kindly amend the LD charges only undelivered portion only and on total Contract. | As per Tender specification
7 | Page NO.6.Clause no. | Sample Submission/Demonstration: TPNODL reserves the right to seek samples or demonstration as sought by Technical team doing the Technical evaluation. | We understand that we need not to submit the sample meters with the techno-commercial bids, after successful evaluation of our techno commercial bids when you asked to arrange the sample to be submitted or demonstrate we will have to arrange for the same, Kindly confirm. | OK,sample shall be Supplied as per tender specification
1.4.9:Sample Submission
8 | Page 6,Qualification criteria. | The bidder should have supplied 10 thousand nos. of Poly phase W/C Meters/Feeder Energy meters | We understand Poly phase meter 10 Thousand nos supplied irrespective of meter current rating u will consider only 10K quantity matters & as we are not in to the manufacturing of Feeder meters, you will consider as we have supplied 10K poly phase meters, Kindly confirm . | OK
9 | Page 15 ,LOT-B | In Lot B , you have asked to quote 10 types of energy meters . | We understand the bidder can quote all 10 items or can quote any items as we are in to manufacturing of 3-Ph 4W LTTV Meters 100/5Amps, LTTV,150/5Amps, & 3-Ph.4-wire 20-100Amp W/C meters & we sincerely request to u we may allowed to quote these three items as above for a broder participation of meter manufacturer in this tender/RC as very limited meter manufacturer available in India who are in the manufacturing of all 10 items of LOT-B, Kindly confirm | as per tender Specificaton

## METER APPLICATION AND BOX
Tender Notice No: TPNODL/OT/2021-22/066
Sr. No. | Detailed Reference to Tata Power Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | Tata Power Response
1 | 2 | 3 | 4 | 5
A | Annexure-1 | Schedule for Items (LOTA) | Please provide the bifurcation of BOQ as per their application, as per HTTV meter there are 3 Type of Specification – Feeder / Consumer / Net meter . Please provide the clarity so that we can provide our offer along with best price in above tender. Request you kindly provide clarity on BOQ.
Sl No | Item Description | Qty |  | Application
1 | 33KV and 11 KV Feeder Energy meter (-/1A, -/110/√3, Cl: 0.2 WH type meters.) as per tech specification | 300 |  | FEEDER METER
2 | 3-ph,4-wire HTTV Meter-/5A,0.2 class without BOX(KWH Meter) | 150 |  | CONSUMER METER
3 | 3-ph,4-wire HTTV Meter-/1A,0.2 class without BOX(WH Meter | 30 |  | CONSUMER METER
4 | 3-ph,4-wire HTTV Meter-/5A,0.5 class without BOX(KWH Meter) | 500 |  | CONSUMER METER
5 | 3-ph,4-wire HTTV Meter-/5A,0.2 class with BOX(KWH Meter) | 30 |  | CONSUMER METER
6 | 3-ph,4-wire HTTV Meter-/5A,0.5 class with BOX(KWH Meter) | 100 |  | CONSUMER METER
7 | 3-ph,4-wire HTTV Meter-/1A,0.2 class with BOX(WH Meter) | 10 |  | NET METER
8 | 3-ph,4-wire HTTV Meter-/5A,0.5 class with BOX(KWH Meter) | 50 |  | NET METER
9 | 3-ph,4-wire LTTV Meter,100/5A,0.5 class with BOX(KWH Meter) | 30 |  | NET METER
10 | 3-ph,4-wire LTTV Meter,150/5A,0.5 class with BOX(KWH Meter) | 30 |  | NET METER
11 | 3-ph,4-wire ,20-100Amp, Whole current meter with BOX | 100 |  | NET METER
B | Annexure-1 | Schedule for Items (LOTA) | As three is requirement of meter Box in Price Schedule , as in tender documents specification of required meter box was not available. Request you kindly clarify for the required meter of Box. | We donn't require BOX for LTCT Meter. For HTTV Meter with Box we require BOX.