## B.1
FORMAT B.1
Format for Technical Pre-Bid Queries
Tender No | TPNODL/OT/2021-22/091
Package Name | SITC FOR 1 PH AND 3 PH METER TEST BENCH
Bidder :
Note : | The said format to be used only for Technical Pre-Bid Query. Any Commercial Query has to be strictly in Format B2 Format for Commercial Pre-Bid Query and sent seperately
Format to be used for query regarding Technical Pre-Qualifcation Requirement, Safety Pre-Qualifcation Requirement, Technical Set of Documnt
Pre-Bid Query has to be sent in editable Excel file fomat only
Pre-Bid Query has to be sent through e-mail in E-Tender System
Sr. No. | Detailed Reference to Tata Power Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | TPNODL Response
1 | 2 | 3 | 4 | 5
2 | Page No. 13 Clause No. 7.3 Delivery Terms | Supply, Installation, Testing and Commissioning of Test Benches shall be completed within 60 days at TPNODL – Odisha, from the placement of release order…… | The requirement is for high precise and capital equipment. Due to current situation of Corona pandemic, there is very much uncertainty for the delivery from the raw material supplier, transportation & custom formalities. Hence we request you to amend the delivery period at least for 180 days instead of existing. | Supply, installation, testing commissioning completion within 90 days,Successful bidder shall submitted the GTP/Drawing within 7 days from date of issuance of order. The total time for TPNODL for approval of GTP /Drawing after first Submission shall be 7 days from the date of submission and 4 days from the date of subsequent submission in case Drawing/GTP are required to be resubmitted.
3 |  |  | Please confirm, for this tender Make in India (MII) procurement policy issued from the government is applicable. Since it supports our nation for become selfdependent. | AS per Tender only.
4 | Clause No:7.3 Delivery Terms | Supply, Installation, Testing and Commissioning of Test Benches shall be completed within 60 days at TPNODL – Odisha, from the placement of PO/LOI. | We can deliver within 60 days. But we recommend you to increase delivery terms to 90 or more than 90 days. Kindly Consider and confirm . | Supply, installation, testing commissioning completion within 90 days,Successful bidder shall submitted the GTP/Drawing within 7 days from date of issuance of order. The total time for TPNODL for approval of GTP /Drawing after first Submission shall be 7 days from the date of submission and 4 days from the date of subsequent submission in case Drawing/GTP are required to be resubmitted.
For 1- Ph Meter Test Bench
5 | Clause no. 5.5: SPECIFICATION OF MULTI SECONDARY VOLTAGE TRANSFORMER/ICT | For 20 position test bench 4 Numbers of ICT would be required and delivered | For each position 1 ICT is required so total 20 ICTs or in case dual ICTs are used then 10 ICTs for 20 position. | Apropriate combination of ICT's/MSVT's to be used so that Phase & Neutral circuit can be tested simultaneously.
6 | Clause no. 7.1: TYPE TEST. | Bidder must submit type test certificate of similar model fully automatic test system as per IS 12346 | Calibration Reports of reference standard meters are sufficient should be acceptable at the time of tender sumission | Type test report for RSM & ICT's/MSVT's should be provided alongwith the bid.
7 | Clause no. 8.0: TYPE TEST CERTIFICATE. | The bidder shall furnish the type test certificates of the meter for the tests as mentioned above as per the corresponding standards. All the tests shall be conducted at CPRI/ERDA as per the relevant standards. For communication testing any national approved laboratory or international acclaimed lab or equivalent will also suffice at the discretion of TPNODL. Type test should have been conducted in certified Test Laboratories during the period not exceeding 5 years from the date of opening the bid. In the event of any discrepancy in the test reports i.e. any test report not acceptable or any/all type tests (including additional type tests, if any) not carried out, same shall be carried out without any cost implication to TPNODL. | Type test reports/ Calibration reports conducted by any NABL Accredited Laboratories should also be acceptable | ok
8 | Clause no. 18.0: DRAWINGS AND DOCUMENTS | f. Type Test Certificates | Calibration Reports of reference standard meters are sufficient should be acceptable at the time of tender sumission | Type test report for RSM & ICT's/MSVT's should be provided alongwith the bid.
For 3- Ph Meter Test Bench
9 | Clause no. 7.1: TYPE TEST. | Bidder must submit type test certificate of similar model fully automatic test system as per IS 12346 | Calibration Reports of reference standard meters are sufficient should be acceptable at the time of tender sumission | Type test report for RSM & ICT's should be provided alongwith the bid.
10 | Clause no. 8.0: TYPE TEST CERTIFICATE. | The bidder shall furnish the type test certificates of the meter for the tests as mentioned above as per the corresponding standards. All the tests shall be conducted at CPRI/ERDA as per the relevant standards. For communication testing any national approved laboratory or international acclaimed lab or equivalent will also suffice at the discretion of TPNODL. Type test should have been conducted in certified Test Laboratories during the period not exceeding 5 years from the date of opening the bid. In the event of any discrepancy in the test reports i.e. any test report not acceptable or any/all type tests (including additional type tests, if any) not carried out, same shall be carried out without any cost implication to TPNODL. | Type test reports/ Calibration reports conducted by any NABL Accredited Laboratories should also be acceptable | OK
11 | Clause no. 18.0: DRAWINGS AND DOCUMENTS | f. Type Test Certificates | Calibration Reports of reference standard meters are sufficient should be acceptable at the time of tender sumission | Type test report for RSM & ICT's should be provided alongwith the bid.
12 | Additional Suggestion | Meter Park Management or Meter History Software: This Software is very necessary to mange the history of meter. It can track record of meters right from purchase uptill the scrapping of the same. This will also be useful in checking the drift in errror of the meter of particular manufacturer or particular batch. All the test benches equipmentscan be connected to this software located at central server. So all the testing data can be centralised for further analysis. This software is also used for deciding scrapping policy of meter or scheduling the testing. | We request you to incorporate this software in the scope of work as it will be beneficial for the utility | As per Tender Only.
For Specification of fully Automatic Twenty position Meter Test bench for Single Phase Meters
13 | Page No. 3 of 20 Clause 4.3 Test to be performed | j) The smart meter switch connection and disconnection over the air commands on no-load condition for all meters simultaneously. k) Smart meter communication testing and switch opening testing. Note: Phase and Neutral circuit should be tested independently without changing connection physically. It should also be possible to test meters like Real time installation (Phase and Neutral elements, together) | We understand that, the requirement is to test Smart meters using asked test bench. Hence it is very much essential that other communication testing features as per IS16444 & IS15959 for SMART meter testing shall be asked. Please note that, there will be no significance of the test system which can’t be able to test special functionality of SMART meters as per above mentioned standards. Hence we are enclosing detail specifications under Annexure B for SMART meter testing as per IS16444 & IS15959 along with floated by various Indian Govt. Utilities vide there tenders. | AS per Tender Only.
14 | Page No. 5 of 20 Clause no. 5.3 Current Amplifier | Sr. No. 8 - VA rating not less than 600VA | It may be noted that the asked VA rating i.e. 600 VA for testing of 20 single phase meters are not sufficient and the test bench will not be able to work with its full loading on such VA. Hence at least 2000 VA shall be asked. | Minimum 600 VA, however sufficient VA should be provided by Test bench Manufacturer so that all meters work at full load.
15 | Page No. 6 of 20 Clause 5.4 Specification of Electronic Reference Meter (RSM) | Sr. No. 11. Display The reference meter shall have following display parameters. (All the parameters also required in actual graphical mode with wave form with THD% value. | The asked equipment is to be operated using Computer as Graphical parameters such as Waveform, Energy, Harmonics shall be asked at PC software. The basic parameters such as voltage current phase angle shall be asked on reference meter display whereas also it may be noted that the offered system will be used thru PC and it shall be asked on PC display. | AS per Tender Only.
16 | Page No. 6 of 20 Clause no. 5.5 Specification of Multi secondary Voltage transformer/ICT | ICT is required for test of MAIN & NEUTRAL Element test together. For 20 position test bench 4 Numbers of ICT would be required and delivered. ICT with Ratio (1:1) & Ratio Error: 0.02% or better, Phase Error: 0.8 Min. or better for current range: 100mA … 120A. Output VA: 60VA/Phase (with single turn) | We request you to amend the ICT specifications as defined in detail vide Cl. No. 5.5 of Three Phase Test bench of this Tender. Also it may be noted that as asked Phase and Neutral circuit testing, at least 7 Nos. ICTs are required for testing of 20 Nos. Single phase meters. 4 nos. ICTs are not sufficient to cater the requirement. Please confirm the same. | OK
17 | Page No. 10 of 20 Clause no. 8.0 Type test | …. For Communication testing any approved laboratory or international acclaimed lab or equivalent will also suffice at the discretion of TPNODL | We understand that type test of energy meters are performed by approved laboratory or International acclaimed laboratory, whereas for utility it is essential that routine testing / functional testing of Smart meter shall be performed as per IS16444 & IS15959. We have enclosed detail specification for functional testing / routine testing under Annexure B. | AS per Tender Only.
18 | Shall be Added | Burden Measurement Function The test bench shall have facility to measure burden (power consumption) as per clause no 6.10.1 of IS16444 (part 1and 2) using suitable methods: The power consumption in voltage circuit has to be measured in following conditions: 1. During idle mode of communication module 2. If a separate module to service a IHD is present 3. During data transmission per communication module. Under each of above mentioned condition, the burden measurement in the voltage circuit shall be performed using Burden measurement unit sequentially on each phase for each meter position of test bench one by one. Burden Measurement unit must be having Clamp on CT to measure current in voltage circuit. The Burden Measurement unit must be having communication with test bench software for fetching the measured results automatically. The measured results reported using associated test system software. The Specification and feature of Burden Measurement Unit shall be as follows: a. Integration of measured power and reporting & Measurement of peak power during the test. b. Automatically reading through test bench associate software. c. Measurement of current in voltage circuit using clamp on CT and without breaking the voltage connection. The burden measurement unit shall also capable to measure power consumption of current circuit of Smart Energy Meter. | It is very much essential to test the burden of SMART Meter as per IS16444 & IS15959. Since due to additional communication module the burden testing of Smart meter becomes very critical for utility purpose. | AS per Tender Only.
7 | Shall be Added | Demonstration The bidder shall arrange demonstration of the tendered functionality of test bench as and when required during technical evaluation at bidder’s cost. If the bidder fail to arrange the same their bid shall not be consider for further evaluation. | The asked test benches are having critical testing requirement i.e. SMART Meter testing. Hence to verify the asked functionality and quality of the equipment, demonstration shall be asked during Technical Evaluation | AS per Tender Only.
For Specification of fully Automatic Twenty position Meter Test bench for Three Phase Meters
19 | Page No. 2 of 21 Clause no. 1.0 Scope | 2nd Paragraph - ….DC and harmonic injector kit…. | A DC injection kit required, but in the documents nowhere specification is defined. Hence we understand that, diode based design as specified in the standard IS13779 and IEC62053-21 is required. Please confirm. | AS per Tender Only.
20 | Page No. 3 of 21 Clause 4.3 Test to be performed | j) The smart meter switch connection and disconnection over the air commands on no-load condition for all meters simultaneously. k) Smart meter communication testing and switch opening testing. Note: Phase and Neutral circuit should be tested independently without changing connection physically. | As per clause no. 2.1 of the GTP of this specifications Smart meter testing with RF NIC as per IS16444 part 1 & 2 has been mentioned. We understand that, the requirement is to test Smart meters using asked test bench. Hence it is very much essential that other communication testing features as per IS16444 & IS15959 for SMART meter testing shall be asked. Please note that, there will be no significance of the test system which can’t be able to test special functionality of SMART meters as per above mentioned standards. Hence we are enclosing detail specifications under Annexure B for SMART meter testing as per IS16444 & IS15959 along with floated by various Indian Govt. Utilities vide there tenders. | AS per Tender Only.
21 | Page No. 4 of 21 Clause no. 5.2 Voltage Amplifier | Sr. No. 9 - VA burden rating Not less than 800VA/phase @ 50 Hz RMS (Should be able to handle load of meter of 7W /meters simultaneously 20 meters without heating) | The asked minimum requirement is very higher side. It shall be asked for 500VA minimum for Three Phase test bench. For smart energy meters it is required 7W Max during communication as per IS16444 power consumption. For 20 nos. of Smart Energy meters it will be 140W which is calculated equivalent to approx. 425VA @PF 0.33 hence considering other droppage at joints, cables etc. of around 75VA it is sufficient 500VA per phase RMS VA burden to test any type of meters. | AS per Tender Only.
22 | Page No. 5 of 21 Clause no. 5.3 Current Amplifier | Sr. No. 8 - VA rating not less than 1200VA/Phase @ 50 Hz RMS | Asked VA rating i.e. 1200 VA to test 20 nos. of three phase energy meters are not sufficient. It may be noted that for ICT - 50 VA already asked and also VA drop at termination, connection to meters, cables shall be added hence for 20 pos. minimum 2000VA/phase is required. Hence it shall be amended. Also note that current circuit having most of the dropped due to terminal resistance, length of cables etc. hence higher VA shall be asked to cater the requirement of 20 nos. meter testing. | Minimum 1200 VA, however sufficient VA should be provided by Test bench Manufacturer so that all meters work at full load.
23 | Page No. 6 of 21 Clause 5.4 Specification of Electronic Reference Meter (RSM) | Sr. No. 11. Display The reference meter shall have following display parameters.(All the parameters also required in actual graphical mode with wave form with THD% value) This is a feature required as per ISO17025/NABL | The asked equipment is to be operated using Computer as Graphical parameters such as Waveform, Energy, Harmonics shall be asked at PC software. The basic parameters such as voltage current phase angle shall be asked on reference meter display whereas also it may be noted that the offered system will be used thru PC and it shall be asked on PC display as per ISO17025/ NABL latest amendment. | AS per Tender Only.
24 | Page No. 6 of 21 Clause 5.5 Specification of ICT | Shall be added ICT shall be having primary and secondary permanently wounded on core with multiple turns for better flux linkage and long term working of ICT with its full capacity. | It may be noted that ICTs available with loose primary and secondary type with one turn are not viable for long term working since due to core properties the flux linkage will reduce with the age of the equipment and not sufficient to pump the desired current on loading of meters. | AS per Tender Only.
25 | Page No. 9 of 21 Clause no. 5.9 SPECIFICATION OF METER MOUNTING RACK | Sr. no. 8 1) Accuracy test for Three phase Meter for phase & Neutral channel for same magnitude of current. 2) Accuracy test for Three phase Meter in case of reverse power for phase & Neutral channel for same magnitude of current. | The requirement is not clear since in three phase meters Accuracy for neutral Element is not applicable. Please clarify if the functionality required for single phase meters testing in three phase test bench. | AS per Tender Only.
26 | Page No. 11 of 21 Clause no. 8.0 Type test | …. For Communication testing any approved laboratory or international acclaimed lab or equivalent will also suffice at the discretion of TPNODCL | We understand that type test of energy meters are performed by approved laboratory or International acclaimed laboratory, whereas for utility it is essential that routine testing / functional testing of Smart meter shall be performed as per IS16444 & IS15959. We have enclosed detail specification for functional testing / routine testing under Annexure B. | AS per Tender Only.
27 | Shall be Added | Burden Measurement Function The test bench shall have facility to measure burden (power consumption) as per clause no 6.10.1 of IS16444 (part 1and 2) using suitable methods: The power consumption in voltage circuit has to be measured in following conditions: 1. During idle mode of communication module 2. If a separate module to service a IHD is present 3. During data transmission per communication module. Under each of above mentioned condition, the burden measurement in the voltage circuit shall be performed using Burden measurement unit sequentially on each phase for each meter position of test bench one by one. Burden Measurement unit must be having Clamp on CT to measure current in voltage circuit. The Burden Measurement unit must be having communication with test bench software for fetching the measured results automatically. The measured results reported using associated test system software. The Specification and feature of Burden Measurement Unit shall be as follows: a. Integration of measured power and reporting & Measurement of peak power during the test. b. Automatically reading through test bench associate software. c. Measurement of current in voltage circuit using clamp on CT and without breaking the voltage connection. The burden measurement unit shall also capable to measure power consumption of current circuit of Smart Energy Meter. | It is very much essential to test the burden of SMART Meter as per IS16444 & IS15959. Since due to additional communication module the burden testing of Smart meter becomes very critical for utility purpose. | AS per Tender Only.
28 | Shall be Added | Demonstration The bidder shall arrange demonstration of the tendered functionality of test bench as and when required during technical evaluation at bidder’s cost. If the bidder fail to arrange the same their bid shall not be consider for further evaluation. | The asked test benches are having critical testing requirement i.e. SMART Meter testing. Hence to verify the asked functionality and quality of the equipment, demonstration shall be asked during Technical Evaluation | AS per Tender Only.
Same points shall be clarified for the relevant clause of GTP.
We are enclosing the Draft specifications for SMART Meter testing as per IS16444 & IS15959 along with specifications floated by various Indian Govt. Utilities. Which are very much essential also it may be noted that vide amendment of Tender No. TPSODL/OT/2021-22/037 recently floated by TPSODL, Smart Meter testing features and Demonstration has been added.
Annexure – B
Testing facilities for communication command for Smart Meters: a. Communicate with all connected Smart meters on its optical port mounted on the test Bench. The test system shall be capable of communicating with the IS15959 /IS16444 compliant Smart meters mounted on the each position over the meter’s optical port simultaneously. The necessary optical head shall be provided for each position on the test system. Response from each connected meter shall be received by associated test system software and reporting of each sent command along with response received from communicable meter shall be done by associated test system software. b. Communicate with Smart meter over its RF communication port. The Test bench shall be integrated with RF (Network Interface Card/gateway/DCU) for communication with all connected Smart Meters. The Manufacturer shall provide necessary provision with test bench to integrate available RF device. Test software shall have provision for received response from each connected meter using RF communication medium. There shall be provision for compare the received output with the response received from the optical ports for each connected meter. The facility shall be provided in the associate test software to report the sent command and response received from each energy meters. c. Functional test The Test system shall perform all the routine functional test as mentioned below simultaneously on all connected meters on the test bench over the communication port. • As per Table A30 of IS15959 Part2 and Table 29 of IS15959 Part3  Associations The associated test system software shall have facility to check object list of the current association of all connected smart meters on meter test bench. The test shall be conducted using each association at a time such as Public Client, MR and US (LLS) via communication port by sending OBIS code to read the object list. The report for each association shall be generated for its accessible attributes i.e. object list using associated test system software.  Data read The associated test system software shall have facility for selecting any five or more readouts from instantaneous parameter list table of IS15959 Part2 (Table A1 and Table A14) and IS15959 Part3 (Table 1 and Table 14). The user can select/ deselect the random parameters from the instantaneous parameters list table as per requirement of the specification using associated test system software. The test shall be conducted using any suitable association such as MR and US (LLS) via communication port and sending OBIS code command for individual parameter read (instantaneous Voltage, PF, frequency, energy etc.). The report for each readout shall be generated for its response from the smart meter using associated test system software.  Connect/disconnect The associated test system software shall have facility to readout the status of connect /disconnect state of all connected meters simultaneously with the test bench. The test shall be conducted using any suitable association such as MR and US (LLS) via communication port and sending OBIS code command for reading the status of load switch. The report for readout status of load switch shall be generated using associated test system software. • Name plate details The associated test bench software shall communicate with the smart meter to read its name plate details as per corresponding table of IS 15959 Part2 (Table A12 and A26), IS15959 Part3 (Table 12 and Table 25). The test shall be conducted once the HDLC connection is establish between client and server using any association at a time such Public Client, MR and US(LLS) via communication and sending OBIS code command for name plate details (Serial No. manufacturer year etc.). The report for response i.e. readout of nameplate details from the smart meter for each OBIS code shall be generated using associated test system software. d. Provision for Burden measurement of the smart meter: The test bench shall have facility to measure burden (power consumption) as per clause no 6.10.1 of IS16444 (part 1and 2) using suitable methods: The power consumption in voltage circuit has to be measured in following conditions: 1. During idle mode of communication module 2. If a separate module to service a IHD is present 3. During data transmission per communication module. Under each of above mentioned condition, the burden measurement in the voltage circuit shall be performed using Burden measurement unit sequentially on each phase for each meter position of test bench one by one. Burden Measurement unit must be having Clamp on CT to measure current in voltage circuit. The Burden Measurement unit must be having communication with test bench software for fetching the measured results automatically. The measured results reported using associated test system software. The Specification and feature of Burden Measurement Unit shall be as follows: a. Integration of measured power and reporting & Measurement of peak power during the test. b. Automatically reading through test bench associate software. c. Measurement of current in voltage circuit using clamp on CT and without breaking the voltage connection. The burden measurement unit shall also be capable to measure power consumption of current circuit of Smart Energy Meter. e. Verification of electrical tamper conditions. Following Electrical Tamper conditions shall be created for its occurrence and restoration by the test bench. The created event shall be verified over the optical port and RF port for connected meters against the test conditions simulated by operator. These tests shall run in automatic mode simultaneously for all connected meters on test bench. Test shall be performed for both occurrence and restoration of corresponding tamper condition. • Voltage missing • Low voltage in any phase • Voltage unbalance • Current missing • Current reversal • Current unbalance The associated test bench software shall have the possibility to show the response received over different communication port such as optical and RF on the same connected Smart meter on the test bench. f. Stress test Test bench shall be able to create the metrological stress conditions to all connected meters on the test bench as mentioned below:- • 10% of 3rd harmonics in phase in current, As per IS13779/14697 • 10% 5th harmonics in voltage and 40% of 5th harmonics in current, • 120% of Vref, As per IS13779/14697 • Imax applied to the meter, As per IS13779/14697 • 60% of Vref, • frequency variation +10% • frequency variation -10% • low PF such as 0.1PF All above conditions shall be simulated by test system and the communication of the smart meter shall be verified in the influenced conditions through performing any one functional test as per above clause no. C. The associate test system software shall having facility to report any discrepancy in the response from meter in normal condition and stressed condition. g. Automatic testing of Communication: The associated test bench system software shall communicate with all connected meters mounted on the test bench either as a single communication command OR combination of several communication commands included in one test sequence i.e. for meter read out and generation/simulation of the tamper conditions/ stress conditions by the test bench. The testing shall be carried out in automatic mode to test the communication correctness on communication ports between all connected smart meters and the test bench.