## B.1
FORMAT B.1
Format for Technical and Commercial Pre-Bid Queries
Tender No | TPNODL/OT/2021-22/111 Dtd.03.12.2021
Package Name | RATE CONTRACT FOR SUPPLY OF SINGLE PHASE 25KVA DISTRIBUTION TRANSFORMER(AL. WOUND)
Bidder :
Sr. No. | Detailed Reference to Tata Power Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks by bidder - Query / Clarification | Tata Power Response
1 | 2 | 3 | 4 | 5
1 | ENG-HV-005/Clause No.5.2/8 of 43 | As per clause 5.2 Winding Connections 1. Primary and secondary winding shall be constructed from high conductivity (Aluminium conductors), Double Paper Covered (DPC) Aluminium conductor with 60% overlap. | We wish to bring to your kind notice that, Option for Super enamel covering is also mentioned in the guidelines for energy efficient distribution transformers, issued by Central Electricity Authority(CEA). So, kindly provide the provision for both DPC and Super enamel covered aluminium conductor also. Incase of DPC covering , winding shall be with 30 % over lap per layer and for TPC 25% overlap per layer. Please amend this cluase. | OK
2 | ENG-HV-005/Clause No.1/2 of 43 | AS PER CLAUSE NO. 1: SCOPE Voltage Ratio:11/√3kV/230V | We wish to bring to your kind notice that, Secondary voltage for single phase transformer as per IS 1180 shall be (240V). Kindly amend this clause as per IS 1180. | Voltage Ratio:11kV/240V (As per revised TS)
3 | ENG-HV-005/Clause No.5.4/13 of 43 | As per Clause no.5.4(8) Transformer shall be designed for the efficiency level of minimum 99.05% for loading range from 20% to 60% at unity power factor. | We request you to kindly allow us to provide the efficiencies as per our design, without exceeding the losses as per IS 1180. kindly confirm. | Accepted, kindly meet the loss requirement as specified in bid document
4 | ENG-HV-005/Clause No.5.5/14 of 43 | As per clause no.5.5(1) The transformer tank shall be of robust construction, round in shape and shall be built up electrically tested welded mild steel plates. As per clause no.5.5(4) For top & Bottom Plate:3.15mm(Min.) For sides:2.5mm(Min.) | We bring to your kind notice that, as per IS 1852 the thickness of Top & Bottom plate shall be 2.5mm (Min.) and for sides: 2.2mm (Min.). We request you to kindly allow us to proceed as per IS 1852. Kindly review and confirm. | Need to comply as per specs
5 | ENG-HV-005/Clause No.4/5 of 43 | As per Clause 4.GENERAL TECHNICAL REQUIREMENTS 19 Power frequency withstand voltage HV kV - 28 | We wish to bring to your kind notice that, 28kV PF on HV side is not possible in case of 11/√3 because one end of HV winding is terminated by 12kV class bushing while the other end of it terminated by 1kV class bushing and finally earthed by tank body. | Both the bushings (Both terminal bushings for HV winding, as per revised TS) should be 12kV class, and the power frequency withstand test should be carried out.
6 | ENG-HV-005/Clause No.5.5/14 of 43 | As per Clause No. 5.5 Transformer tank & Tank construction The tank shall be fabricated by welding at corners. No horizontal and vertical joints in tank side walls. | As per the specification, the tank shape is round type. There are no corners in the round tank. One continuous vertical welding from top to bottom of the side wall of the round tank is required to join the sheet to form round shape. | OK
7 | ENG-HV-005/Clause No.5.5/15 of 43 | As per Clause No. 5.5 Transformer tank & Tank construction 7. The tank cover shall be conical shape (slope of at least 15 degree taking horizontal plane as reference). | We will provide the top cover as dome shape without accumilating the water on surface. | OK
8 | ENG-HV-005/Clause No.5.8/18 of 43 | As per Clause No. 5.8 LV box with MCCB | Please provide the LV connection diagram (sketch) to clarify each and every part of connection from LV bushing to MCCB and MCCB to further. Similarly on neutral side. | Drawings will be finalised during technical evalution, as of now if there any clarification required refer to "Clause No. 5.8 LV box with MCCB"
9 | ENG-HV-005/Clause No.4.17/5 of 43 | As per Clause No. 4.17, Percentage Regulation 4% As per Clause No. 5.4. 9. Percentage regulation shall be less than 4% at 0.8 power factor | Percentage regulation value will be arrived based on achieved No Load, load Losses w.r.t. Energy Efficiency level 2 losses but it Is not a fixed value | OK
10 | ENG-HV-005/Clause No.5.11/19 of 43 | As per Clause No. 5.11 Default Oil shall be Mineral Oil only if not specified/asked for other oil. | No special note was found. Hence it is presumed that the oil is mineral oil. All parameters as per clause no. 5.11 – Mineral Oil | OK
11 | ENG-HV-005/Clause No.5.5.13/15 of 43 | As per Clause No. 5.5.13 Minimum oil level mark shall be embossed inside the tank (at 25° C). | As per latest amended IS 1180-2014, “ Minimum position corresponds to the operating temperature of 30 degree C. Hence, kindly allow to proceed as per IS 1180-2014 | OK
12 | ENG-HV-005/Clause No.5.8.4/18 of 43 | As per Clause No. 5.8.4 The Single phase MCCB box shall be provided with suitable size of Al bus bar w.r.t minimum current density (Calculated) of 1 A / sq.mm. Inside for further distribution of supply. | Kindly amend as “Single phase MCCB Box shall be provided with suitable size of Al busbar w.r.t. maximum current density (calculated) of 1 A/sq. mm, inside for further distribution of supply.” | OK
13 | ENG-HV-005/Clause No.5.17/22 of 43 | As per Clause No. 5.17 A signal light shall be provided to give information about the loading condition of the transformer. It shall forewarn any overloading (not momentary overloading) problem at the installation. | Kindly allow for proceeding without signal light | Need to comply as per specs only
14 | ENG-HV-005/Clause No.5.18.14/23 of 43 | As per Clause No. 5.18.14 Palm connector on LV side | Kindly confirm if any alternate arrangement will be acceptable. | Need to comply as per specs only
15 | ENG-HV-005/Clause No.6.2/24 of 43 | As per Clause No. 6.2 Primary markings : 1U & 2u, neutral 2n | Kindly allow to provide terminal markings as per IS 1180 standard. | OK
16 | TPNODL/OT/2021-22/111 Dtd.03.12.2021/ Clause no. 3.9/Type Tests/ Page No.13 | The type tests specified in TPNODL specifications should have been carried out within five years prior to the date of opening of technical bids and test reports are to be submitted along with the bids. If type tests carried out are not within the five years prior to the date of bidding, the bidder will arrange to carry out type tests specified, at his cost. The decision to accept/ reject such bids rests with TPNODL. | We request you to allow us for submission of similar or higher rating type test reports during the evaluation stage. We will conduct and submit the type test reports as per Tender specification and offered design after receipt of RC at our cost without affecting the delivery schedule. Kindly review and confirm. | OK
17 | TPNODL/OT/2021-22/111 Dtd.03.12.2021/ General Conditions of Contract/Clause no. 8.0. Security cum Performance Deposit Page No. 8 of 47 | Associates shall submit within 15 days from the effective date of issue of PO/RC, Security Performance Bank Guarantee (SPBG) in the format as per Annexure B of this document from banks acceptable to TPNODL for: (a) 5% of the PO value if purchase order value is more than Rs 5 Crores. (b) 10% of the PO value if purchase order value is less than Rs 5 Crores. This shall remain valid till the end of the Guarantee Period of contract, plus one month. | We request you to amend the clause as per the below: Associates shall submit within 15 days from the effective date of issue of PO/RC, Security cum Performance Bank Guarantee (SPBG) in the format as per Annexure B of this document from banks acceptable to TPNODL for: (a) 1% of the PO value if purchase order value is more than Rs 5 Crores. (b) 3% of the PO value if purchase order value is less than Rs 5 Crores. This shall remain valid till the end of the Guarantee Period of contract, plus one month. | Clause remain same as per GCC
18 | TPNODL/OT/2021-22/111 Dtd.03.12.2021/ Clause no. 7.4/Warranty period/ Page No.16 | Guarantee/Warranty Period of the supplied material shall be 5 years from the supply of the material at TPNODL store/site. | We bring to your kind notice that, many DISCOMs has adopted the Guarantee/ Warranty period of the Transformers for a period of 36 months from the date of supply of Transformer. Kindly consider the same and amend the warranty period as requested above. | Need to comply as per specs, Guarantee/Warranty Period of the supplied material shall be 5 years from the supply of the material at TPNODL store/site.
19 | Transformer tank & tank Construction | In Clause No. 1 is mentioned The transformer tank shall be of robust construction, round in shape and shall be built up of electrically tested welded mild steel plates and In Clause No.2 The tank shall be fabricated by welding at corners | These two ponits contrdict each other, kindly specify circular tank only. | The tank shape should be circular only ( Need to provide heat dissipation calculation for circular shape)
20 | General technical Requirement | In Pont No. 17 there is mentioned Percentage Regulation is 4% | No other conditioned are mentioned and confusing as % implendance is mentioned as 4% the regulation will be as per the calculation. Kindly clarify. | %impedance is 4 and percentage regulation is as per losses
21 | Type test certificates | Required as per Tender Specification, manufacturer should have valid type test report of same design and rating, not more than 5 years. | We have valid type test up to 250 KVA, 11/0.433 and 16 KVA 11/.250 KV AL.wound Transformer. 1st time this type of tender floated by TPNODL in odisha.We undertake that we will carry out Type Test at ERDA/CPRI at our own cost after receive of order. Kindly allow to participate the tender. | OK