## B.1
FORMAT B.1
Format for Technical Pre-Bid Queries
Tender No | TPNODL/OT/2021-22/059 Dt. 19.08.2021
Package Name | Rate Contract for Supply of 1-Phase & 3-Phase Meter Box
Note : | Pre-Bid Query has to be sent in editable Excel file fomat only
Sr. No. | Detailed Reference to TPSODL Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | TPNODL Response
1 | 2 | 3 | 4 | 5
1 | clause 5.4 of Technical specification Single Phase Meter Box | The Overall dimension of meter box is mentioned 300*250*120 mm | Please clarify exact size of the Box (Dimensions) with tolerance. Also clarify clearance required | The Overall dimension of meter box is 300*250*120 mm . Tolerance 2%. Minimum clearance 50 mm ( all side)
2 | clause 5.7 of Technical specification Single Phase Meter Box | Two nos. GI Hinges Minimum length 50 mm | Please clarify Hinge type box required or Push fit Type Box required | only Hinge type
3 | clause 5 of Technical specification Single Phase Meter Box | Push Button and provision for Optical Probe | Please clarify Push button and provision for optical port required or not | Push button and provision for optical port required
4 | Page Number 9 | Sample | Please share the exact address for the delivery of the samples | Meter Management Group(MMG), 1st Floor, Block-A NORTHERN ODISHA DISTRIBUTION LIMITED. Corporate Office, Januganj, Balasore-756019.
5 | 5.0 GENERAL CONSTRUCTIONS/Single pahse | 5.3-The box shall be provided with meter mounting arrangement along with MS plate on top for mounting the meter from different manufacturers, 5.4- The meter shall be mounted with the help of MS plate such that it is centrally placed in the box and there shall be clearance of 50 mm between the meter and top of the box. | MS Plate is not required as enclosure is having mounting pillers for Genus 1P meter. Clearance is available of 15 mm between the meter and top of the box. | MS plate is required and Minimum clearance shall be 50mm between the top of meter and box.
6 | 5.0 GENERAL CONSTRUCTIONS//Single pahse | 5.4- A minimum clearance of 50 mm shall be maintained on both sides, between meter and box. The overall dimension of meter box shall be length -300mm, With 250mm, Depth 120mm | 30MM clearances available from both sode & top side instead of 50mm. 15mm from front & 10mm from back. 75mm from T block. Dimension of meter box shall be length -237mm, With 217.5mm, Depth 85mm | Not acceptable . Pls follow technical specifications.
7 | 5.0 GENERAL CONSTRUCTIONS//Single pahse | 5.5- Nylon gland of internal diameter of approx 25 mm shall be provided for I/C and O/G cables of size armoured 2Cx10/25 sq.mm or as approved by purchaser. The holes for I/C and O/G cables shall be provided in left and right side of meter box at bottom. | 2 nos Plastic cable Gland PG29 will be provided at bottom side of box instead of Left & right side. | The holes for I/C and O/G cables shall be provided in left and right side of meter box at bottom.
8 | 5.0 GENERAL CONSTRUCTIONS/Single pahse | 5.6- The number of pillers to be provided in box as per TPC different type of meters. Bidder shall provide meter mounting piller accordingly in meter box with modification in their mould without any extra cost. | No need for any modification as enclosure is already hiaving mounting pillers to mount genus meter | The number of pillars to be provided in box as per TPC different type of meters( Genus, HPL, Schneider etc.). Bidder shall provide meter mounting pillar accordingly in meter box with modification in their mould without any extra cost.
9 | 5.0 GENERAL CONSTRUCTIONS//Single pahse | 5.7-The box cover shall be fixed to the base through two nos. Metallic Hinges ( Approx. length 50mm) The arrangement of the hinges shall be provided on left side of the box. | Concealed hinge 2 nos with min 24mm length will be provided on left side of the box as per tender sample | Two nos. Metallic Hinges ( Approx. length 50mm)
10 | 5.0 GENERAL CONSTRUCTIONS/Single pahse | 5.8- For holding and sealing the box, four U-shaped latches of approx..size 25 mm shall be provided on three side of box ( two on right side and one each on top and bottom side).The latch shall be GI with minimum thickness of 1.2 mm. | Meter box have 2 Nos U-shaped latches With size 25mm, Thickness Minimum 1 mm on the right side of Meter box. | Pls follow technical specifications.
11 | 5.0 GENERAL CONSTRUCTIONS/Single pahse | 5.11- Suitable overlapping (20 mm) shall be provided between base and cover to avoid access to the meter or its accessories inside the meter box by any means after sealing the box. | 10mm Overlapping will be provided between base and cover | Pls follow technical specifications.
12 | 5.0 GENERAL CONSTRUCTIONS//Single pahse | 5.12- Box shall be provided with 1 no. earthing nut and bolt of size M8x35 mm on the left hand side in the base of meter box for providing earth connection. | We will provide (1 nos) earthing bolt assembly of size M6x25mm on the left hand side in the base of meter box | Bolt size: M8x35 mm.
13 | 6.0 Name plate and Marking/Single pahse | The meter box shall be provided with durable and legible name plate, Meter Sl.No. to be printed on the meter name plate | Information can be provided through laser on enclosure top. | Pls follow technical specifications.
14 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | 10 Construction features of the box a) Clear inside dimensions of meter box i. Length 460mm ii. Width 340mm iii. Depth 170mm With 2% tolerance (With minimum clear space of 450x330 without any tolerance) | i. Length 385mm ii. Width 245mm iii. Depth 138mm With 5% tolerance | Pls follow technical specifications.
15 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | b) Minimum clearance between meter and box on all sides : 50 mm c) Min. Clearance from meter on Top of meter mounting plate : 35mm d) Minimum clearance from back of meter to base : 10mm | 30MM clearances available from both sode & 110 mm from top side instead of 50mm. 50mm from front & 5mm from back. 75mm from T block. | Pls follow technical specifications.
16 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | e) Earthing arrangement Nut & bolt 1 Numbers with M8x 35 or 40mm long | 1 no. earthing nut and bolt of size M6x25 mm | Pls follow technical specifications.
17 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | g) 4 number GI U shape latches having 1.2mm thick | 4nos S.S. U latch shape having 1.0mm thk | Pls follow technical specifications.
18 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | j) Cover overlapping on base a) Inside- 25 mm overlapping at hinges sides, top and bottom side and 20 mm overlapping at pad lock side. b) Outside overlapping 20mm through out border | 10mm Overlapping will be provided between base and cover Pad lock arrangement not available | Pls follow technical specifications.
19 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | l) Meter mounting plate as per clause no.5.4 GI plate of 1.2m thick for meter mounting provided on Top side (without sharp corners) | MS Plate is not required as enclosure is having mounting pillers for Genus 3P meter. | Pls follow technical specifications.
20 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | n) Hinges Three nos. GI Hinges having 1.2 mm thickness and Minimum length 30 mm | This arrangement is required for SMC boxes. As we are providing plastic enclosure, there is no use of this option. | Pls follow technical specifications.
21 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | p) Antenna mounting provision GI square piece of around 30x30mm to be riveted/ fixed inside on bottom face of box at around 60mm distance from right side | Antenna mounting provision not available so not provided | Antenna mounting provision is required .Pls follow technical specifications.
22 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | s) Location of earthing bolt On left Sides (when viewed from front) & bolt is fixed & engaged within gland through GI sheet 1.2mm from inside. | Earth bolt at left side & without GI sheet arrangement | Pls follow technical specifications.
23 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | The earth connectivity plate between incoming gland and earth bolt provided with 1.2mm thick GI | Due to plastic box earth connectivity plate between incoming gland and earth bolt not required | Pls follow technical specifications.
24 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | 5.5- The design of the meter box shall be such as to easy facilitate easy wiring and access to meter terminals. Nylon gland of internal diameter of approx. 30 mm shall be provided for I/C and O/G cables of size 4Cx25 sq.mm or as approved by purchaser. The holes for I/C and O/G cables shall be provided in left and right side of meter box at bottom. | 2 nos Plastic cable Gland will be provided at bottom side of box instead of Left & right side. | The holes for I/C and O/G cables shall be provided in left and right side of mete
25 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | The box shall have suitable modem mounting arrangement on the right hand side in the base of meter box for mounting the modem from different manufacturers with the help of base plate. | Modem Mounting arrangement onTop side of Box without Plate, Genus mounting suitable | Pls follow technical specifications.
26 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | 5.3-The box shall be provided with meter mounting arrangement along with MS plate on top for mounting the meter from different manufacturers, having different mounting dimensions. | MS Plate is not required as enclosure is having mounting pillers for Genus 3P meter. | Pls follow technical specifications.
27 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | 5.6- The number of pillers to be provided in box as per TPC different type of meters. Bidder shall provide meter mounting piller accordingly in meter box with modification in their mould without any extra cost. | No need for any modification as enclosure is already hiaving mounting pillers to mount genus meter | Pls follow technical specifications.
28 | 4.0 GENERAL TECHNICAL REQUIREMENTS/3 Phase | The meter box shall be provided with durable and legible name plate, Meter Sl.No. to be printed on the meter name plate | Information can be provided through laser on enclosure top. | Pls follow technical specifications.
29
30
31
32
33
34
35
36
37
38
39
40
41