## Sheet1
Tender | TPNODL/OT/2021-22/049 Dt. 07.08.2021
Package | RATE CONTRACT FOR SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs in TPNODL Area
Sr. No. | Detailed Reference to TPnODL Technical Document. Please specify Document No / Clause No / Page No | Description as per Bid Document | Remarks - Query / Clarification | TPNODL Response
1 | 2 | 3 | 4 | 5
1 | 1.1 Scope of work / Pdf page no 7 of 225 | ITC of Relay- Differential Relay, ITC of Relay- Feeder Protection relay / ITC of Relay- Master trip relay | Supply of any material related to Retrofitting like Blanking plate ,necessary wires ,testing Kit and setting calculation is not in our scope. Integration of scada will not be in our scope however necessary support like preration of ICD /CID will be consider in our scope as part of supervision of commissioning. Please confirm | As Per Tender Documents We Required All Need Things To Complete This Job.
2 | 7.4/Warranty Period /pdf sheet no.16 | Guarantee/Warranty Period of the supplied material shall be of 18Months from the date of supply of material at TPNODL/as per technical specification attached separately with this tender. | We understand that the gurantee shall start after the commissioining of each item seperately and shall be 18 months from the date of supply. | As Per Tender Documents Min 48-60 months GAURANTEE.
3 |  |  | As per caluse 15. GUARANTEE, page no 137, warranty period is mentioned as 48 months from the date of commissioning or 60 months from the date of last supplies made under the contract, whichever is earlier. Please confirm the warranty period. | As Per Tender Documents Min 48-60 months GAURANTEE.
4 | 5.12/MFM/pdf sheet no.103 | Energy Meter | We understand that 0.2s class MFM is acceptable for this requirement. | yes
5 | 5.12/MFM/pdf sheet no.103 | Energy Meter | Pls specifiy any preferred Make & Model for the MFM | 1-SATEC PM 130 PLUS,2-ACCORD MFM-02, 3-SELEC-383,376,374 4 - SCHNIDER em6400, em6436, em6400ng. 5-Secure Elite 440
6 | 5.12/MFM/pdf sheet no.103 | Supply and Integration of Energy Meters with Software for centralized meter data reading shall be in supplier’s scope. Supplied Software shall have independent for meter make or OEM to retrieving the meter data. | The quantity of the metering software shall be part fo supply BoQ. | yes
7 | 5. GENERAL TECHNICAL REQUIREMENTS: / Aux Supply: pdf sheet no. 127 | If the auxiliary supply drifts, 2 alarms may be triggered: High set point alarm, adjustable from 105 % to 150 % of rated supply (maximum 275 V). Low set point alarm, adjustable from 60 % to 95 % of rated supply (minimum 20 V). | proposed relay doesn't have D.C. supply supervision features. Please accept the same. | Required Watchdog Function
8 | 5. GENERAL TECHNICAL REQUIREMENTS: / Tripping curve For Phase over current and Earth Fault: pdf sheet no. 128 |  | Proposed relay have following characteristics, DTL, IEC-NI, IEC-VI, IEC-EI, IEC-LTI, ANSI-EI, ANSI-MI, ANSI-VI. Please consider the same | required
9 | 5. GENERAL TECHNICAL REQUIREMENTS: / Network and machine diagnostics: pdf sheet no. 129 | Phase fault and earth fault trip counters | Proposed relay have CB trip counter. Please consider the same | ok
10 |  | Harmonic distortion (THD), current and voltage Ithd, Uthd | Harmonic details can be obtained from waveform recording. Please consider the same. | Wave form have
11 |  | Phase displacement | We assume phase angle details are required. Please confirm the same. | required
12 |  | Running hours counter / operating time | Proposed relay doesn't have running hour counter. Same can be obtained from event log (Time between CB close & CB open). Please accept the same. | Event & Sponatanious
13 |  | Through current It1, It2, It3 | We asuume, Restrain current / Bias current details are required. Please confirm | Confirm
14 | 5. GENERAL TECHNICAL REQUIREMENTS: / Setting of Phase over Current: pdf sheet no. 129 | Definite time Setting 0.001 to 24 In, Time delay 0.001 s to 300 s | As per GUARANTEED TECHNICAL PARTICULARS/ Page no 139 of the technical specification, Definite time Setting is 0.05 to 24 In, Time delay 0.05 s to 300 s which is also complied by our proposed relay. Please confirm the same. | As Per Tender Document Required Definite time Setting 0.001 to 24 In, Time delay 0.001 s to 300 s
15 |  | IDMT Setting 0.001 to 2.4 In, Time Delay.0 to 12.5 sec | As per GUARANTEED TECHNICAL PARTICULARS/ Page no 139, of the technical specification, IDMT Setting is 0.05 to 2.4 In, Time Delay 0.1 to 12.5 sec. which is also complied by our proposed relay. Please confirm the same. | As Per Tender Document Required IDMT Setting 0.001 to 2.4 In, Time Delay.0 to 12.5 sec
16 | 5. GENERAL TECHNICAL REQUIREMENTS: / Setting of Earth fault / Sensitive earth fault : pdf sheet no. 129 | IDMT Setting 0.001 to 1 In0 (min. 0.1 A) | Minimum setting is our proposed relay is 0.005 X In (0.005A for 1A CT secondary, 0.025A for 5 A CT secondary). Please accept the same. | As Per Tender Document Required IDMT Setting 0.001 to 1 In0 (min. 0.1 A)
17 |  | IDMT Time Delay 0.0 to 12.5 sec | As per GUARANTEED TECHNICAL PARTICULARS/ Page no 139, of the technical specification, TMS For IDMT E/F protection is 0.1 to 12.5 sec which is also complied by our proposed relay. Please confirm the same. | As Per Tender Document Required IDMT Time Delay 0.0 to 12.5 sec
18 | 5. GENERAL TECHNICAL REQUIREMENTS: / Setting of Breaker Failure: pdf sheet no. 129 | Presence of current - 0.01 to 2 In Operating time 0.0 s to 3 s | As per GUARANTEED TECHNICAL PARTICULARS/ Page no 139, of the technical specification, Presence of current for CBFP is 0.2 to 2 In, Operating time 0.05 s to 3 s which is also complied by our proposed relay. Please confirm the same. | As Per Tender Document Required Presence of current - 0.01 to 2 In Operating time 0.0 s to 3 s
19 | 5. GENERAL TECHNICAL REQUIREMENTS: / Setting of Negative sequence / unbalance: pdf sheet no. 129 | Definite time setting - 0.1 to 5 Ib/10% to 500% Time Delay-0.0 to 300 s | setting range for 46 protection function is 10% to 400%. Please accept the same. | Accept
20 |  | IDMT Setting 0.1 to 1 Ib/ 10% to 100% Time Delay 0.0 to 1s | minimum TMS setting for 46 protection function is 0.025. Please accept the same. | Accept
21 | 5. GENERAL TECHNICAL REQUIREMENTS: / Setting of Thermal overload: pdf sheet no. 130 | Time constant Heating T1: 1 to 600 min Cooling T2: 5 to 600 min Alarm and tripping set points 0 to 300 % of rated thermal capacity Maximum equipment temperature 60 to 200 °C (140 °F to 392 °F) | Proposed relay supports thermal overload protection function (49) as per IEC characteristics. Application note & setting guideline is attached herewith. Please accept the same. | Accept
22 | 5. GENERAL TECHNICAL REQUIREMENTS: /Setting of Differential Protection (T-87) : pdf sheet no. 130 | Restraint on energization Current threshold - 1 to 10 % Time. | Please provide details on the same. | As per tender document
23 | 5. GENERAL TECHNICAL REQUIREMENTS: /Setting of Over fluxing(V/Hz): pdf sheet no. 130 | Set Point 1.03 to 2 pu Definite time Setting -0.0 to 20000 s IDMT Setting - 0.0 to 1250 s | Proposed relay have following characteristics Definite time Setting 0.0 to 14400 s IDMT Setting - User defined characteristics with 6 point setting. Please accept the same. | Accept
24 | 5. GENERAL TECHNICAL REQUIREMENTS: /Setting of Under voltage (L-L or L-N) : pdf sheet no. 130 | Set point 5 to 100 % of Unp Time Delay - 0.05 to 300 s | U/V setting range is 5 -200V. Please consider the same. | Accept
25 | 5. GENERAL TECHNICAL REQUIREMENTS: /Configuration Method: pdf sheet no. 130 | Relay shall be configurable from HMI as well as software through Laptop. | IEC 61850 related configuration (i.e. RCB, Data set, Goose related configuration) are possible through laptop & relay software only. Please accept the same. | Accept
26 | 5. GENERAL TECHNICAL REQUIREMENTS: /Push buttons: pdf sheet no. 131 | Functional keys should be available for separate trip command. | Proposed relay have dedicated keys for CB Trip & Close command. Please accept the same. | Accept
27 | 5. GENERAL TECHNICAL REQUIREMENTS: /Output contacts: pdf sheet no. 131 | The relay shall have 20 NO + 4 changeover potential free and heavy duty programmable contacts. Min 12 no’s relay output contacts shall be provided for specific function outputs for alarm, trip & trip circuit supervision. All output contacts should be freely programmable. | As per the requirement minimum 12 contacts are required for specific function outputs, however as per the same spec it also mentioned all contacts should be freely configurable please clarify. | for below 33kv - 20 bi and 12 bo required with fast operating contacts and trip coil supervision coil in adition.
28 | 5. GENERAL TECHNICAL REQUIREMENTS: /Output contacts: pdf sheet no. 131 | The relay shall have 20 NO + 4 changeover potential free and heavy duty programmable contacts. | Proposed relay have 16 nos + 2 change over contact. Please consider the same. | OK
29 | 5. GENERAL TECHNICAL REQUIREMENTS: /LCD Display: pdf sheet no. 132 | Relay shall have minimum 4 line LCD backlit display | As per Point no 5. GENERAL TECHNICAL REQUIREMENTS: / Display/ Page no 127 of this specification, Advanced UMI with graphical LCD screen is required. Please confirm the same. | Advanced UMI with graphical LCD screen
30 | Communication protocol/Transformer Diff Relay /pdf sheet no.132 | Details of Numerical relay communication ports are as follows. Front: Ethernet port Rear: IEC 61850 (for integration of relays with SCADA and accessing DR from remote through Tata Power automation WAN) | We shall offer Protection relay with front USB Type port and rear dual RJ45 port.Pls acknowledge | Front port should be RJ45,USB to USB,Serial Port but at Rear Port RJ45 2-3
31 | Special requirement/Transformer Diff Relay /pdf sheet no.133 | One complete set of Relay configuration tool (Laptop, communication cable, Moxa, Manual) to be supplied for every 5 no’s lot of Relays, and pre-configured relay software along with all device configuration software to be pre- installed. | We propose - One complete set of relay configuration tool(Laptop, communication cable, Moxa, Manual) to be supplied stationwise.Pls ackowledge | ok but pls provide 2 no's of comunnication cable moxa,manual
32 | 17. GUARANTEED TECHNICAL PARTICULARS:/Settings of protection functions /pdf sheet no.139 | Choice of restraint - Conventional & Self-adapting. | Proposed relay have Dual slope biased restraint characteristics. Please consider the same. | Accept
33 | 18. RECOMMENDED IED’s MAKE/MODELS: / pdf sheet no.140 | Recommended model from Siemens | We will propose a relay model which will comply most of the technical requirement as per the TPNODL technical specification. Please accept the same. | Dependability is the degree of certainty that the relay will operate and functioning correctly.
34 | 5. GENERAL TECHNICAL REQUIREMENTS: /Elements: pdf sheet no.145 | Practically any PSM selection and any TMS selection with resolution of 0.001 lowest at 0.01) | PSM selection is complying to the range as specified in the GTP of this specification. Resolution of the TMS selection also complying the the GTP of this specification (Page no 155). Please confirm the same. | Go through as per tender document
35 | 5. GENERAL TECHNICAL REQUIREMENTS: /Operating Characteristics selectable: pdf sheet no.146 | 1. IDMT IEC – 3 Sec. 2. IDMT - 1.3 sec. 3. IEC Very Inverse 4. IEC Normal Inverse 5. IEC Extremely Inverse 6. IEC Definite time 7. IEC User defined inverse 8. IEC Long time inverse | Proposed relay have following characteristics, DTL, IEC-NI, IEC-VI, IEC-EI, IEC-LTI, ANSI-EI, ANSI-MI, ANSI-VI. Please consider the same | Ok
36 | 5. GENERAL TECHNICAL REQUIREMENTS: /Time multiplier setting for O/C & E/F for IDMT: pdf sheet no.146 | 0.0 to 1.0 in steps of 0.01 | Minimum setting for TMS is 0.025. Please accept the same. | Minimum setting for TMS should be 0.001 min
37 | 5. GENERAL TECHNICAL REQUIREMENTS: /Broken Conductor Protection : pdf sheet no.146 | The relay shall be capable of Broken Conductor Protection. Setting range should be I2/I1 from 0.001 to 1.0 | As per GUARANTEED TECHNICAL PARTICULARS/ Page no 155, The r Broken Conductor Protection. Setting range should be from 0.5 to 1.0 which is also complied by our proposed relay. Please confirm the same. | As Per Tender Document Required Setting range should be I2/I1 from 0.001 to 1.0
38 | 5. GENERAL TECHNICAL REQUIREMENTS: /Output contacts : pdf sheet no.146 & input contacts pdf sheet no.146 | The relay shall have 10 NO + 2 changeover potential free and heavy duty programmable contacts.The relay shall have 24 no’s of binary input contacts with pickup value 80% of input voltage. | As per GTP, page no 156 & page no 157, 6 + 2 Change over contact & 8DI is required. We assume as per general technical requirement total 24DI & 12 DO is required. Please Confirm. | We assume as per general technical requirement total 24DI & 12 DO is required
39 | Communication protocol/OC & EF Relay /pdf sheet no.148 | Details of Numerical relay communication ports are as follows. Front: Ethernet port Rear: IEC 61850 (for integration of relays with SCADA and accessing DR from remote through Tata Power automation WAN) | We shall offer Protection relay with front USB Type port and rear dual RJ45 port.Pls acknowledge | rear 2nos Ethernet port for PRP network Rear: IEC 61850 (for integration of relays with SCADA and accessing DR from remote through Tata Power automation WAN)
40 | Special requirement/OC & EF Relay /pdf sheet no.149 | One complete set of Relay configuration tool (Laptop, communication cable, Moxa, Manual) to be supplied for every 5 no’s lot of Relays, and pre-configured relay software along with all device configuration software to be pre- installed. | One complete set of relay configuration tool(Laptop, communication cable, Moxa, Manual) to be supplied stationwise.Pls ackowledge | Accept But Front port should be RJ45,USB to USB,Serial Port and Rear Port RJ45 2-3
41 | 18. RECOMMENDED IED’s MAKE/MODEL:/ pdf sheet no.159 |  | Recommended make model is different in page no 19 & Page no 159. Please confirm the same | not found any relation
42 |  | Recommended model from Siemens | We will propose a relay model which will comply most of the technical requirement as per the TPNODL technical specification. Please accept the same. | As per tender document pls acknowledge our technical requirement.
43 | 4.7/Response Time and IO Capabilities /pdf sheet no.175 |  | Please provide a clarification regarding the qty mentioned. We understand that this is Total IO capacities of the substation RTU. Whether all this inputs will be hooked up with RTU | hard wired I/O points need to mention
44 | 4.9/Data Concentrator (DC) or Remote Terminal Unit (RTU) /pdf sheet no.176 | There should not be more than 16 IEDs per Ethernet Port and 8 IEDs per Serial Port. | Our offered RTU having very fast procerssor speed.So, upto 50 IEDs can be connected on each Ethernet port without any compromise on the processor speed. | As per RFP
45 | 4.9/Data Concentrator (DC) or Remote Terminal Unit (RTU) /pdf sheet no.177 | All the cards/modules of the RTU/DC must have conformal coating for protection against harsh environments. | Offered RTU has been tested for corrosive environment as per DIN EN 60068-2-60 Method 4.So, separate conformal coating is not required.Pls acknowledge | conformal coating required all relay and RTU
46 | 4.9/Data Concentrator (DC) or Remote Terminal Unit (RTU) /pdf sheet no.178 | It should have complete redundant hardware design including CPU, Power Supply, Communication Modules and Bus Interface Unit/Card. | Pls clarify the redundnacy scope in RTU | PRP required in evey substation and relay need to considred like this
47 | 4.10/ Ethernet Switch/ pdf sheet no.179 | Each switch should have minimum of 24 Ports | As per pdf page no 3 & 20, 12 port Ethernet switch is required. Please confirm the total no of port for ethernet switch. | minimum of 24 Ports
48 | 4.11/ Fibre Optic Cable / pdf sheet no.180 |  | Please provide the details - Qty, Length etc. | This will be known at the time of detail engineering.Or bidder can go for site visit to know the details
49 | 4.11/ CAT – VI / pdf sheet no.180 |  | Please provide the details - Qty, Length etc. | This will be known at the time of detail engineering.Or bidder can go for site visit to know the details
50 | 4.11/ RS 485 Cable / pdf sheet no.180 |  | Please provide the details - Qty, Length etc. | This will be known at the time of detail engineering.Or bidder can go for site visit to know the details
51 | 14.0/Training/pdf sheet no.187 | The scope of training | Training scope related to no. of persons,no. of days shall be clearly mentioned.We understand that the training may be conducted at site/TPNODL office in single batch | Training scope related to min 5 no's person and min 3 to 4 days .Training conducted at factory with R&D Team.
52 | Annexure-III/pdf sheet no.197 | Line CRP Requirement | We understand that the Line Feeder CRP is with BCPU only.So, pls explain the scope of PDR | back up and main protection for EHV ckt
53 | Annexure-III/Transformer Monitoring Unit /pdf sheet no.197 | A transformer monitoring (TMU) | We understand that the same is not in bidder scope of suppply | yes
54 | General |  | Pls share the Feeder type,Quantity details of the sub-station where the RTUs are to be installed | Go through as per tender document
55 | General |  | Pls share the SLD of sub-stations under present scope | This will be known at the time of detail engineering.Or bidder can go for site visit to know the details
56 | General |  | Pls share the IEDs details and its communication interface for each station | Go through as per tender document
57 | General | Spares Quantity | The requirement of mandatory spares shall be part of tender BoQ | 20% spare meterials or one complete unit equavalent to 20% of total quantity
58 | General | 11kV CRP Type | We understand that 11kV system is a Switchgear based requirement as per Annexure-III(pdf sheet 197)So, 11kV CRP shall not be applicable | We are procuring 11kv CRP panels for switch gear availble in our door.
59 | General | CRP Type | As we have to offer BCPU based CRP as per Annexure-III(pdf sheet 197).So, conventional type metering,mimic,control switches,indication lamps and annunciation shall not be applicable | TNC, 86 RELAY LR SWITCH AND INDICATION LAMP REQUIRED .
60 | General | 6 Master Trip Relay | Pls confirm the contact details required for Master Trip Relays | 10-8 NO/ 2NC SET- REST
61 | General | RTU Remote station integration | We understans that our scope shall be limited upto station end only.Any integration with SCADA/ADMS is not in prsent scope. | successful bidder has to integrate these RTUs with Mini scada ( It will be ready at the time of end of the RTUs work)
62 | General |  | We request TPNODL to share a typical System Architecture for this tender | It will be shared to Successful bidder while detail engineering.
63 | General | Process Bus based requirement | We understand that Process Bus based BCPU/IED or system is not applicable under present package | yes
64 | General | RTU I/Os | Pls specify the Hardwired I/O for RTUs at each station | hard wiring required for 60 I/O ( DI=30, DO=20, AI=10)
65 | General | Master trip relay | Please provide the details of existing master trip relays. | It will be shared to Successful bidder while detail engineering.
66 | General Recommendation | Relay | As per specification IEC 61850 is required. We propose to consider IEC 61850 edition 2 which is latest as EOL instruction is already deployed. | As per specification IEC 61850 is required BOTH EDITION 1&2
67 | General Recommendation | Rear communication port - Relay | As per Automation specification (Page no 173) IEC 62439-3 Parallel Redundancy Protocol is required. We propse to consider 2 nos of ethernet port which should supports PRP & HSR | YES
68 | General Recommendation | Relay | Considering the installation of the relays in coastal areas, we propose all the protection relays to have conformal coated PCB increase the over all life of the protection relays. | CONFORMAL coating required all relay
69 | General Recommendation | Relay | We propose IP54 (Front) enclosure protection for all protection relays | OK
70 | General Recommendation | Transformer protection Relay | We propose the transformer differential protection relay shall have site selectable 1A/5A CT input. | YES
71 | General Recommendation | HV Feeder O/C & E/F protection Relay | As per spec Relay shall have minimum 4 line LCD backlit display. We propose to consider Advance UMI with SLD display as mentioned for Transformer differential relay in this specification. | consider Advance UMI with SLD display WITH Breaker operation enabled
72 | General Query | Transformer protection Relay | We assume Trafo differential relay with 8CT input & 4VT input will be accepted for this requirement from TPNODL. Please confirm. | 8CT , REF, SEF core and 8VT
73 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - Clause - 7.1 Special Conditions of Contract | After finalization of tender, Rate Contract shall be issued on successful bidder with a validity period of 12 Months. Prices shall remain firm till validity of issued rate contract. Within the validity of rate contract and as per requirement of material, release order shall be issued time to time. TPNODL reserves the right to extend this RC according to the performance, quality of the material for 06 Months. | We presume rate contract clauses are not applicable in this package and same shall be not valid wherever mentioned in tender documents. Bidders have to quote the items as per Corrigendum-1_OT_049 quantities-price schedule and same shall be used for bid evolution. Kindly confirm. | All the clause are applicable as the tender terms & conditions
74 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - Clause - 7.1 Special Conditions of Contract | Within 15 days of Rate Contract issuance by TPNODL, it is the responsibility of BA to get manufacturing clearance and CAT-A issued from TPNODL. In case BA does not get necessary approvals for issuance of CAT-A within mentioned timelines, then TPNODL reserve the right to cancel issued rate contract / release order and also reserve the right to forfeit EMD / PBG. | We presume rate contract clauses are not applicable in this package and same shall be not valid wherever mentioned in tender documents. Bidders have to quote the items as per Corrigendum-1_OT_049 and same shall be used for bid evolution. Kindly confirm. Even if RC applicable than mentioned conditions shall be applicable from Order release. Kindly confirm. | All the clause are applicable as the tender terms & conditions
75 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - Clause - 7.1 Special Conditions of Contract | Post award of rate contract, Business Associate (BA) shall submit applicable Performance Bank Guarantee as per GCC within 15 days. PBG applicable shall 5% of Rate Contract Value. PBG submitted, shall be released after completion of applicable minimum 18months or guarantee period plus one month. | We understand PBG shall not be applicable from RC award. PBG shall be applicable for Release Order as per clause- 7.5 Payment Terms . Kindly confirm. | PBG shall be applicale from RC award
76 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - Clause - 7.5 Payment Terms | Note: - PBG-3 % of Contract value shall be applicable for this contract. The validity of PBG shall be till the warranty period plus one month. | We understand Clause - 7.1 Special Conditions of Contract is not applicable for PBG. And this the valid clause. Kindly confirm. | PBG shall be 5% of the RC value
77 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - GCC Clause - 8.0 SECURITY CUM PERFORMANCE DEPOSIT | Associates shall submit within 15 days from the effective date of issue of PO/RC, Security Performance Bank Guarantee (SPBG) in the format as per Annexure B of this document from banks acceptable to TPNODL for: | We understand SCC Clause - 7.5 Payment Terms is valid & supersede this GCC clause. Kindly confirm. | PBG-5 % of Contract value shall be applicable for this contract. The validity of PBG shall be till the warranty period plus one month.
78 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - GCC Clause - 13.2 Guarantee Period | Guarantee Period will be 48 Months from the Date of Commissioning or 60 months from the date of delivery of final lot of supplies made, whichever is earlier. | We understand SCC Clause - 7.4 Warranty Period is valid & supersede this GCC clause. Kindly confirm. | 60 months from the date of commissiong
79 | Approved relay make & model list- 2020 | TATA Power-DDL substations | We understand, TPDDL is a typo mistake and it shall be referred as TPNODL. | yes
80 | Corrigendum-1_OT_049 - page no-18-20 | Price Schedule - RTU Quantity 24 nos. | Please provide the no of substation in which these 24nos. RTU to be installed. | will be shared with successful bidder
81 | Corrigendum-1_OT_049 - page no-18-20 | Price Schedule - Installation Testing & Commissioning along with Integration with SCADA (if any)- 33KV & 11KV Control Relay Panel | We understand, there are no SCADA/SAS/RTU system at existing/new sub-station. All CRP & loose relay being supplied in this package shall be integrated with 24nos new RTU are being supplied in present package at different stations. Kindly confirm. | yes
82 | Corrigendum-1_OT_049 - page no-18-20 | Price Schedule -Installation Testing & Commissioning along with Integration with SCADA (if any)- 33KV & 11KV Control Relay Panel | We presume supply & commissioning of MFM, Energy Meter, TMU, FIREWALL, Any type of control/LV power cable as part of CRP or loose are not part of present scope. Kindly confirm. | It is in bidders scope
83 | Corrigendum-1_OT_049 - page no-18-20 | Price Schedule - Installation Testing & Commissioning and ITC part | Kindly elaborate & specify the scope cover under this line items. We have excluded below in our scope of supply & services. Any unloading of panels , shifting of panels, any existing panel dismantling, any type of civil work, erection of panel, any type of cable laying & termination in CRP/RTU panel. | Its in Bidder scope ,Bidder has to arrange all these things, Price has to be included
84 | Corrigendum-1_OT_049 - page no-18-20 | Price Schedule - ITC part of relay | We presume space is available in existing CRP for new relay mounting. Kindly confirm. | as per tender document ITC of relay is part of job
85 | Corrigendum-1_OT_049 - page no-18-20 & ANNEXURE-II - AUTOMATION SPECIFICATION FOR 33KV-11KV POWER SYSTEM NETWORK IN NEW GRID SUBSTATION BASED ON IEC 61850 | Price Schedule & Signal List | As relays are configured for Bay level monitoring and Control. We don’t envisaged any physical digital input, digital output, analog input, analog output hardwire on RTU. Relays will communicate to RTU and RTU will communicate to Central control system and all these digital input, digital output, analog input, analog output data will be fetched from relay. Please confirm | hard wiring required for 60 I/O ( DI=30, DO=20, AI=10)
86 | Corrigendum-1_OT_049 - page no-18-20 & ANNEXURE-II - AUTOMATION SPECIFICATION FOR 33KV-11KV POWER SYSTEM NETWORK IN NEW GRID SUBSTATION BASED ON IEC 61850 | Price Schedule, BOQ & Signal List | 1. Please provide the station wise IEDs/MFM/Any hardwired I/O details. 2. Please provide the station wise SLD & Layout. | This will be known at the time of detail engineering. Or bidder can go for site visit to know the details
87 | Corrigendum-1_OT_049 - page no-18-20 & ANNEXURE-II - AUTOMATION SPECIFICATION FOR 33KV-11KV POWER SYSTEM NETWORK IN NEW GRID SUBSTATION BASED ON IEC 61850 | Communication interface & Protocol | Any work at TPSDOL control centre/MCC/BCC is not in our scope. Bidder scope covers configuration of RTU for integration with control centre/MCC/BCC TPSDOL at station end only. | Go through as per tender document
88 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - TECHNICAL SPECIFICATIONS FOR 33kV/11kV POWER SYSTEM CRP Clause - 5.2 Constructional Features | However, the width of panels that are being offered to be placed in existing switchyard control rooms, should be in conformity with the space availability in the control room. | As no sub-station details (layout etc.) has been provide about existing stations. Buyer has to ensure the space availability in control room. | ok
89 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - TECHNICAL SPECIFICATIONS FOR 33kV/11kV POWER SYSTEM CRP Clause - 5.12 Energy Meters | Supply and Integration of Energy Meters with Software for centralized meter data reading shall be in supplier’s scope. Supplied Software shall have independent for meter make or OEM to retrieving the meter data. | We understand supply of energy meters, associated items & its integration with existing central metering system is not part of present scope of work. Since it is not part of price schedule/BOQ. Kindly confirm. | ok
90 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - TECHNICAL SPECIFICATIONS FOR 33kV/11kV POWER SYSTEM CRP Clause - 16.0 Ethernet Switches | Guaranteed Technical Particular - Should have minimum of 12 Ports, number of switches minimum 2. | As per Corrigendum-1_OT_049. Supply of 24-48V DC Ethernet Switch (12 Port) is 96nos. However 24nos new RTU are being supplied as per PS. We understand bidders have to supply 2nos for station EFS & 2nos fro CRP. Kindly confirm | Confirm
91 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - TECHNICAL SPECIFICATIONS FOR 33kV/11kV POWER SYSTEM CRP Clause - 16.0 Spares, Accessories and Tools | Spares for Project job for New Grids / Bay Extension - 20% spare material required for every item like TNC switch and other switches, indicating lamps, terminal blocks and any other auxiliary relays, if used. | We understand this spare clause is not applicable for this package since spares are missing form boq/price schedule bid evaluation. If spares are required kindly add the each type of spare in BOQ/price schedule. Kindly confirm. | 20% spare meterials or one complete unit equavalent to 20% of total quantityshould be supplied and Bidder will quote this amount included with main items.
92 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Technical Requirement | GTP - Output contacts & Input contacts | We understand differential relay shall have 24nos. Input & 24 no's Output (20 NO plus 4nos. change over) contact. Kindly confirm. | CONFIRM
93 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Technical Requirement | Restricted Earth Fault | We understand REF functionality on high or low impedance should have software programmable and any hardware changes shall not be required. Kindly confirm. | ref - high or low is mentioned in ordering code of relay . Need to be considered while tendering.
94 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Technical Requirement | Phase over current | We understand directional O/C & E/F shall be required along with differential protection. Kindly confirm. | directional O/C & E/F shall be required along with differential protection this for main protection .for backup directional relay also required
95 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Technical Requirement | Second & Fifth harmonic blocking feature | Second & Fifth harmonic blocking feature is not mentioned in specification. But same is required to avoid any unwanted tripping during transformer charging. Kindly confirm & include in TS. | Second & Fifth harmonic blocking feature is required
96 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Technical Requirement | CT saturation detection technique during external fault | CT saturation detection technique during external fault feature is not mentioned in specification. But same is required to avoid any external fault tripping. Kindly confirm & include in TS. | required
97 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Technical Requirement | Harmonic distortion (THD), current and voltage Ithd, Uthd Phase displacement | Harmonic distortion (THD), current and voltage Ithd, Uthd Phase displacement features are not required for trafo protection. Our relay does not have this features. Kindly exclude the same from TS. | Wave form have
98 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Technical Requirement | Relay shall have minimum 4 line LCD backlit display | We offer the relay with 3line backlit display as our all relay comes with this feature. Kindly amend the same in TS. | 4 line required main protection relay
99 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Technical Requirement | GTP - Communication protocol- Each relay shall have IEC 61850 port which can be used for SCADA applications. | As per spec clause 4.3 system architecture The link between Bay Level IEDs and RTU/DCU shall be as per IEC 62439-3 Parallel Redundancy Protocol. And PRP has not been mentioned in any other part of specification. We understand IEC 61850 PRP (Parallel Redundancy Protocol) is envisaged for the relay. Kindly confirm . | PRP required in every substation and relay need to considered like this
100 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 5.0 Special Requirement | One complete set of Relay configuration tool (Laptop, communication cable, Moxa, Manual) to be supplied for every 5 no’s lot of Relays, and pre-configured relay software along with all device configuration software to be pre- installed. | We understand this clause is not applicable for this package. Since these items are missing form boq/price schedule bid evaluation. If required kindly confirm the total requirement. | One complete set of relay configuration tool(Laptop, communication cable, Moxa, Manual) to be supplied stationwise.Pls acknowledge
101 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - STANDARAD TECHNICAL SPECIFICATION OF DIFFERENTIAL RELAY FOR TRANSFORMER Clause - 15. GUARANTEE: | In the event any defect is found by the Company up to a period of 48 months from the date of commissioning or 60 months from the date of last supplies made under the contract, whichever is earlier. | We understand SCC Clause - 7.4 Warranty Period is valid & supersede this clause. Kindly confirm. | Commercial team will reply
102 | STANDARAD TECHNICAL SPECIFICATION For HV FEEDER DIRECTIONAL & NON- DIRECTIONAL OVER-CURRENT & EARTH FAULT PROTECTION RELAY Clause - 5.0 Technical Requirement | Output contacts & Input contacts | As per GTP clause - 5.0 relay shall have 24nos. Input & 12nos. (10 NO plus 2nos. change over) of Output heavy duty programmable contacts.. Min 12 no’s relay output contacts shall be provided for specific function outputs for alarm, trip & trip circuit supervision. All output contacts should be freely programmable. However as per GTP clause - 17.0 relay shall have 8nos. Input & 8nos. of Output contact with recoded model GE P127. We understand relay required with minimum 24nos. Input & 22nos. of Output contact to cover the requirement of min 12 no’s relay output contacts shall be provided for specific function outputs for alarm, trip & trip circuit supervision. Kindly confirm. | AS PER TENDER DOCUMENT
103 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs -HV FEEDER DIRECTIONAL & NONDIRECTIONAL OVER-CURRENT & EARTH FAULT PROTECTION RELAY Clause - 5.0 General Technical Requirement | Broken conductor(I2/I1) with minimum 2 stages | For broken conductor we have setting rage which can address broken conductor protection philosophy in one stage itself. Kindly accept the same | ACCEPT
104 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs -HV FEEDER DIRECTIONAL & NONDIRECTIONAL OVER-CURRENT & EARTH FAULT PROTECTION RELAY Clause - 5.0 General Technical Requirement | Relay shall have minimum 4 line LCD backlit display | We offer the relay with 3line backlit display as our all relay comes with this feature. Kindly amend the same in TS. | 4 line required main protection relay
105 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs -HV FEEDER DIRECTIONAL & NONDIRECTIONAL OVER-CURRENT & EARTH FAULT PROTECTION RELAY Clause - 5.0 General Technical Requirement | Minimum 2 setting groups | We recommend 4 setting group minimum for Feeder Protection. For Transformer protection 4 setting group has been requested , we recommend 4 setting group minimum for Feeder Protection as well. Please confirm | Confirm
106 | STANDARAD TECHNICAL SPECIFICATION For HV FEEDER DIRECTIONAL & NON- DIRECTIONAL OVER-CURRENT & EARTH FAULT PROTECTION RELAY Clause - 5.0 Technical Requirement | GTP - Communication protocol- Each relay shall have IEC 61850 port which can be used for SCADA applications. | As per spec clause 4.3 system architecture The link between Bay Level IEDs and RTU/DCU shall be as per IEC 62439-3 Parallel Redundancy Protocol. And PRP has not been mentioned in any other part of specification. We understand IEC 61850 PRP (Parallel Redundancy Protocol) is envisaged for the relay. Kindly confirm . | PRP required in every substation and relay need to considered like this
107 | STANDARAD TECHNICAL SPECIFICATION For HV FEEDER DIRECTIONAL & NON- DIRECTIONAL OVER-CURRENT & EARTH FAULT PROTECTION RELAY Clause - 5.0 Special Requirement | One complete set of Relay configuration tool (Laptop, communication cable, Moxa, Manual) to be supplied for every 5 no’s lot of Relays, and pre-configured relay software along with all device configuration software to be pre- installed. | We understand this clause is not applicable for this package. Since these items are missing form boq/price schedule bid evaluation. If required kindly confirm the total requirement. | Two complete set of relay configuration tool(Laptop, communication cable, Moxa, Manual) to be supplied in favoured to TPNODL
108 | STANDARAD TECHNICAL SPECIFICATION For HV FEEDER DIRECTIONAL & NON- DIRECTIONAL OVER-CURRENT & EARTH FAULT PROTECTION RELAY Clause - 15. GUARANTEE: | In the event any defect is found by the Company up to a period of 48 months from the date of commissioning or 60 months from the date of last supplies made under the contract, whichever is earlier, | We understand SCC Clause - 7.4 Warranty Period is valid & supersede this clause. Kindly confirm. | AS PER TENDER Document
109 | Tender Ref-049-SITC of 33kV and 11kV Control & Relay Panels along with SITC of IEDs - Automation Specifications for 33kV/11kV Power System Network in New Grid Station based on IEC-61850 Protocol | 4.2-General System Design, 4.3-System Architecture - The Substation Automation System (SAS) & IEC 62439-3 Parallel Redundancy Protocol requirement | We understand Substation Automation System (SAS) & IEC 62439-3 Parallel Redundancy Protocol requirement is applicable for this package. Kindly confirm. | As per Tender document , refer the below clause The link between Bay Level IEDs and RTU/DCU shall be as per IEC 62439-3 Parallel Redundancy Protocol on dual star network topology with a redundant managed switched Ethernet communication infrastructure.
110 | Automation Specifications for 33kV/11kV Power System Network in New Grid Station based on IEC-61850 Protocol clause 4.9 Data Concentrator (DC) or Remote Terminal Unit (RTU) | The RTU/ Data Concentrator should support min. of 4 SNTP Servers and broadcast the time sync to the IEDs at Bay level | We suggest to modify the requirement as 2nos. SNTP server support. | accept
111 | Automation Specifications for 33kV/11kV Power System Network in New Grid Station based on IEC-61850 Protocol clause 18.1 Support & Services | Services to be included during guarantee period 1. Guarantee shall be for 60 months from the date of commissioning or 66 months from the date of supply. | We understand SCC Clause - 7.4 Warranty Period is valid & supersede this clause. Kindly confirm. | Go through as per tender document guarantee shall be min 60 month date of supply.
112 | Annexure II-Technical Specification : clause 20.1 RTU/DC - Guaranteed Technical Particular -14 | It should have complete redundant hardware design including CPU, Power Supply, Communication Modules and Bus Interface Unit/Card. | We presume & recommend, redundant hardware design including CPU, Power Supply, Communication Modules and Bus Interface Unit/Card must be achieved via two separate physical RTU (If RTU redundancy is required). Kindly confirm. | As per tender specification redundency is must , bidder can go through any model without any price implication to TPNODL
113 | Annexure II-Technical Specification : clause 20.2 Ethernet Switch - Guaranteed Technical Particular-9 | Should have minimum of 24 Ports | As per Corrigendum-1_OT_049. Supply of 24-48V DC Ethernet Switch (12 Port ) as per TPNODL Specs. Kindly confirm Bidders have to quote the Ethernet switch ports configuration as per spec or BOQ. | 12 port Ethernet switch will be ok.
78 | TPNODL/OT/2021-22/049 Dt. 07.08.2021 & Annexure – I on page no. 18 |  | please provide your confirmation that the Partner of Approved Makes ( Siemens / ABB / Alstom/ Schneider / L&T) can quote for Control & Relay Panel for subjected Tender. | Yes
79 | TPNODL/OT/2021-22/049, Annexure – I |  | BOQ Sl. No. 2,4,6,10,11,12,17 and 18 – Number of sub-stations involved in this project. | Number substaions are as per the number of qty mentioned against each line item. For Qty please refer corrigendum-1.49
80 | TPNODL/OT/2021-22/049, Annexure – I |  | As per BOQ – Integration with SCADA – Please let us know the existing SCADA make | SCADA under procurement stage. Make shall be either ABB/Siemens/GE/L&T

## Sheet2
SPARES
S.NO | Item | Qnty