## Sheet1
Your Tender NIT No. TPNODL/OT/2021-22/102 dtd. 19.11.2021 RC for supply of 11KV & 33KV Metering Unit in TPNODL Area.
Sr. No. | Clause | TPNODL Point | KAPCO Reply | TPNODL's Response
1 | As per Annexure-VI ACCEPTANCE FORM FOR PARTICIPATION IN REVERSE AUCTION EVENT point no. 12 | The original price bids of the bidders shall be reduced on pro-rata basis against each line item based on the final all inclusive prices offered during conclusion of the auction event for arriving at Contract amount. | Instead of allowing us to bid only the total package price, kindly allow us to submit bid against each line item. | It will considered before conduction of RA upon mangement aooroval.
2 | As per Tender documents of clause no. 5 Special Conditions of Contract | Delivery period shall be 60 days from date of receipt of release Order. | Delivery will be 90 days from receipt of RO. Justification:- i. procurement of Raw material-15days ii. manufacturing & Testing-45 days iii. DI from TPNODL-12 days iv. PDI-8 days v. transit time-10 days Total-90 days Alternately date of offer of material for inspection be taken as date of delivery for LD calculation purpose. | As per Tender only.
3 | As per Tender documents of clause no. 12 Special Conditions of Contract | TPNODL keeps the right to repeat the order within 12 months at same price. | Accepted as with IEEMA PV circular only. | As per Tender only.
4 | As per technical specification of 33kV Unit of clause no. 5.6 | Pantone 2727C/TPNODL Blue With thickness not less than 80 microns. | Tank surface as per GTR serial no. 20 is mentioned as Painted, whereas in clause no 5.6. its mentioned as Hot Dip Galvanized. Please confirm whether your requirement is Painted or Hot dip galvanized Tanks? | hot-dip galvanization & thereafter power coating as per cl no 5.6
5 | As per technical specification of 33kV Unit of clause no. 7.2 (A & B) clause of Routine tests & Acceptance tests. | Partial discharge test in accordance with IS 11322-1985 | As per IS: 2705/1992 & 3156/1992 clause 9.1.2 (e) Partial Discharge test not applicable for 11kV & 33kV Units. Its applicable for 72.5kV & above voltage and so be removed from testing clause. | As per Tender only.
6 | As per technical specification of 33kV Unit of clause no. 7.2 (D) clause of For Enclosure: | Enclosure tightness test, as per clause 7.3.7.2 of IEC 61869 Part-1 | Enclosure tightness test not applicable as a routine test as per IS:2705/1992 & 3156/1992 | Per IS:2705/1992 & 3156/1992
7 | As per Annexure-I of 11kV CT-PT Unit of ratio 5/5A, 10/5A, 15/5A,25/5A & 100/5A | As per Annexure-II of 11kV CT-PT Unit of Technical Specification of ratio 10/5A, 15/5A, 20/5A, 100/5A & 200/5A | Kindly clarify which type ratio of your requirement. As the ratio of CT-PT Unit are not same in Annexure-I & II. | As per Annexure -I 11kV CT-PT Unit of ratio 5/5A, 10/5A, 15/5A,25/5A & 100/5A
8 | As per Annexure-I of 33kV CT-PT Unit of ratio 10/5A, 15/5A, 20/5A, 30/5A & 50/5A | As per Technical specification of clause no. 4.0 point no. 4.2.1 three ratio mentioned is 200/5A, 300/5A & 400/5A | Kindly specify STC rating for other ratios. | Same of other CT Ratio ( 26.3 kA for 1 sec )
9 | As per technical specification of 33kV CT-PT Unit of clause no 5.4 | The equipment shall be supplied with 6 Nos. outdoor single terminal, porcelain bushings of reputed make (as approved by TPNODL) without arcing horns, 3 nos. for incoming and 3 nos. for outgoing, with Copper/ Brass studs as per the rating. | Clause no. 4.4.5 says tinned cooper & Clause no. 5.4 says Tinned plated brass. Please confirm the what material of conductor is required. Generally aluminum ACSR connector are used. | AS per Tender only.
10 | 1.7 Qualification Criteria Clause : 1.7.1 | 1.7.1 The bidder should have average annual turnover of 3 Cr. or above for last 3 Financial Year. Bidders have to submit copy of audited Balance Sheet and P & L Account in this regard. | We are Micro Scale Unit. Approve our request of 50% Turnover i.e @ Rs. 1.5 Cr. | Qualification Criteria shall be as mentioned in the NIT
11 | 1.7 Qualification Criteria Clause : 1.7.1 | 1.7.1 The bidder should have average annual turnover of 3 Cr. or above for last 3 Financial Year. Bidders have to submit copy of audited Balance Sheet and P & L Account in this regard. | OR Give us permition to offer only 11KV Metering Cubicles (Full Quantity). So, that Turnover requirement will be half that required for both 11KV and 33 KV Metering Cubles. | Qualification Criteria shall be as mentioned in the NIT
12 | GENERAL CONDITIONS OF CONTRACT FOR SUPPLY ORDERS. 9.4 MSME Development ACT 2006 | Business Associates falling in MSME category shall submit the Tender Fee when participating in TPNODL tenders. However, they are eligible to submit concessional EMD at 50% of the EMD otherwise applicable | We are MSME Unit. We are eligible to submite EMD @ 50% | Yes. Business Associate shall submit the self-undertaking of registration in MSME category at the time of bidding as well as on an annual basis to TPNODL, enabling them to avail the consequent benefits, failing which TPNODL may take appropriate action against such defaults.